## RL7
NO | PHASE 2 TAG | PHASE 2A TAG | OEM TAG | JB | DESCRIPTION | P&ID | ROOM | PANEL | ORDER | SLOT | CH | MODULE TYPE | MODULE P/N | RANGE | DEVICE INSTALLED | DEVICE TAGGED | CA INSTALLED | RACEWAYS COMPLETE | WIRE PULLED | WIRE TERMED | WIRE TAGGED | POINT TO POINT | IO CHECK | IO GOOD | NOTES
0 | RL7-LFT-101-1:I.PT00 | RL7-LFT-101-1:I.PT00 |  |  | E-STOP OK | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 0 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1 | RL7-LFT-101-1:I.PT01 | RL7-LFT-101-1:I.PT01 |  |  | THERMAL FAULT HYDRAULIC | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 1 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
2 | RL7-LFT-101-1:I.PT02 | RL7-LFT-101-1:I.PT02 |  |  | THERMAL FAULT LIFT | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 2 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
3 | RL7-LFT-101-1:I.PT03 | RL7-LFT-101-1:I.PT03 |  |  | STOP BUTTON | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 3 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
4 | RL7-LFT-101-1:I.PT04 | RL7-LFT-101-1:I.PT04 |  |  | LIFT UP BUTTON | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 4 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
5 | RL7-LFT-101-1:I.PT05 | RL7-LFT-101-1:I.PT05 |  |  | LIFT DOWN BUTTON | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 5 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
6 | RL7-LFT-101-1:I.PT06 | RL7-LFT-101-1:I.PT06 |  |  | TURN RIGHT SWITCH SELECTOR | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 6 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
7 | RL7-LFT-101-1:I.PT07 | RL7-LFT-101-1:I.PT07 |  |  | TURN LEFT SWITCH SELECTOR | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 7 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
8 | RL7-LFT-101-1:I.PT08 | RL7-LFT-101-1:I.PT08 |  |  | CLAMP SWITCH SELECTOR | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 8 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
9 | RL7-LFT-101-1:I.PT09 | RL7-LFT-101-1:I.PT09 |  |  | RELEASE SWITCH SELECTOR | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 9 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
10 | RL7-LFT-101-1:I.PT10 | RL7-LFT-101-1:I.PT10 |  |  | SERVICE BUTTON | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 10 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
11 | RL7-LFT-101-1:I.PT11 | RL7-LFT-101-1:I.PT11 |  |  | SENSOR RIGHT | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 11 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
12 | RL7-LFT-101-1:I.PT12 | RL7-LFT-101-1:I.PT12 |  |  | SENSOR BOTTOM | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 12 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
13 | RL7-LFT-101-1:I.PT13 | RL7-LFT-101-1:I.PT13 |  |  | SENSOR TOP | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 13 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
14 | RL7-LFT-101-1:I.PT14 | RL7-LFT-101-1:I.PT14 |  |  | SENSOR SAFE BOTTOM | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 14 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
15 | RL7-LFT-101-1:I.PT15 | RL7-LFT-101-1:I.PT15 |  |  | SENSOR SAFE TOP | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 1 | 15 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
16 | RL7-LFT-101-2:I.PT00 | RL7-LFT-101-2:I.PT00 |  |  | SENSOR MIDDLE | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 2 | 0 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
17 | RL7-LFT-101-2:I.PT01 | RL7-LFT-101-2:I.PT01 |  |  | SENSOR LEFT | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 2 | 1 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
18 | RL7-LFT-101-2:I.PT02 | RL7-LFT-101-2:I.PT02 |  |  | BEFORE TILT | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 2 | 2 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
19 | RL7-LFT-101-2:I.PT03 | RL7-LFT-101-2:I.PT03 |  |  | NEXT MACHINE READY | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 2 | 3 | 24 VDC DI | 5069-IB16
20 | RL7-LFT-101-2:I.PT04 | RL7-LFT-101-2:I.PT04 |  |  | GATE OPEN SENSORS | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 2 | 4 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
21 | RL7-LFT-101-2:I.PT05 | RL7-LFT-101-2:I.PT05 |  |  | GATE CLOSED SENSORS | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 2 | 5 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
22 | RL7-LFT-101-2:I.PT06 | RL7-LFT-101-2:I.PT06 |  |  | BOTTON OPEN | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 2 | 6 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
23 | RL7-LFT-101-2:I.PT07 | RL7-LFT-101-2:I.PT07 |  |  | BUTTON CLOSED | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 2 | 7 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
24 | RL7-LFT-101-3:O.PT00 | RL7-LFT-101-3:O.PT00 |  |  | MOTOR FORWARD | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 0 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
25 | RL7-LFT-101-3:O.PT01 | RL7-LFT-101-3:O.PT01 |  |  | MOTOR REVERSE | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 1 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
26 | RL7-LFT-101-3:O.PT02 | RL7-LFT-101-3:O.PT02 |  |  | HYDRAULIC ON | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 2 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
27 | RL7-LFT-101-3:O.PT03 | RL7-LFT-101-3:O.PT03 |  |  | VALVE GRIP CLAMP | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 3 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
28 | RL7-LFT-101-3:O.PT04 | RL7-LFT-101-3:O.PT04 |  |  | VALVE GRIP RELEASE | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 4 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
29 | RL7-LFT-101-3:O.PT05 | RL7-LFT-101-3:O.PT05 |  |  | VALVE TURN RIGHT | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 5 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
30 | RL7-LFT-101-3:O.PT06 | RL7-LFT-101-3:O.PT06 |  |  | VALVE TURN LEFT | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 6 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
31 | RL7-LFT-101-3:O.PT07 | RL7-LFT-101-3:O.PT07 |  |  | RESET LAMP | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 7 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
32 | RL7-LFT-101-3:O.PT08 | RL7-LFT-101-3:O.PT08 |  |  | LIFT UP LAMP | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 8 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
33 | RL7-LFT-101-3:O.PT09 | RL7-LFT-101-3:O.PT09 |  |  | LIFT DOWN LAMP | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 9 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
34 | RL7-LFT-101-3:O.PT10 | RL7-LFT-101-3:O.PT10 |  |  | STOP LAMP | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 10 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
35 | RL7-LFT-101-3:O.PT11 | RL7-LFT-101-3:O.PT11 |  |  | SERVICE LAMP | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 11 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
36 | RL7-LFT-101-3:O.PT12 | RL7-LFT-101-3:O.PT12 |  |  | BYPASS VALVE | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 12 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
37 | RL7-LFT-101-3:O.PT13 | RL7-LFT-101-3:O.PT13 |  |  | LINK IN | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 13 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
38 | RL7-LFT-101-3:O.PT14 | RL7-LFT-101-3:O.PT14 |  |  | LINK OUT | DG6800 | PROC | RL7-LFT-RIO1 | 2 | 3 | 14 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
40 | RL7-TNK-101-ZSC-04 | RL7-TNK-101-ZSC-04 |  |  | BREDDO MIXER SWING ELBOW IN PROCESS POSITION | DG6806 | PROC | RL7-BRED-RIO1 | 11 | 3 | 6 | 24 VDC DI | 5069-IB16
41 | RL7-TNK-101-ZSC-05 | RL7-TNK-101-ZSC-05 |  |  | BREDDO MIXER SWING ELBOW IN SANITATION POSITION | DG6806 | PROC | RL7-BRED-RIO1 | 11 | 3 | 7 | 24 VDC DI | 5069-IB16
42 | RL7-AGC-104-PBL-01 | RL7-AGC-104-PBL-01 | PB906161 | JIC11B, OS11A | FRESH AUGER CART 1 PUMP E-STOP PB PILOT LIGHT | DG6807 | PROC | RL7-FAGC1-RIO1 | 8 | 6 | 8 | 24 VDC DO | 5069-OB16
43 | RL7-CNV-107-XV-08 | RL7-CNV-107-XV-08 |  |  | INCLINE PIVOT AUGER 3 SANITATION VALVE OPEN SOLENOID | DG6809 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 12 | 24 VDC DO | 5069-OB16
44 |  | RL7-CNV-107.M2 |  |  | INCLINE PIVOT AUGER 3 HYDRAULIC PUMP ENABLE | DG6809 | MCC | RL7-INTSL-RIO1 | 18 | 14 | 7 | 24 VDC DO | 5069-OB16
45 | RL7-AGC-201-ZSS-02 | RL7-AGC-201-ZSS-02 | PRS1106211 |  | DISCHARGE AUGER CART COVER CLOSED SAFETY INPUT CH1 | DG6817 | CHILL | RL7-DAGC1-RIO1 | 14 | 2 | 0 | 24 VDC SI | 5069-IB8S
46 | RL7-AGC-201-ZSS-02 | RL7-AGC-201-ZSS-02 | PRS1106211 |  | DISCHARGE AUGER CART COVER CLOSED SAFETY INPUT CH2 | DG6817 | CHILL | RL7-DAGC1-RIO1 | 14 | 2 | 1 | 24 VDC SI | 5069-IB8S
47 | RL7-AGC-201-PSL-01 | RL7-AGC-201-PSL-01 | PRG1107191 | JIC13B | DISCHARGE AUGER CART PRESSURE REGULATOR LOW PRESSURE SWITCH | DG6817 | CHILL | RL7-DAGC1-RIO1 | 14 | 4 | 2 | 24 VDC DI | 5069-IB16
48 | RL7-CNV-201-YI-01 | RL7-CNV-201-YI-01 |  |  | CHUB MACHINE RUNNING | DG6818 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 13 | 24 VDC DI | 5069-IB16
49 | RL7-CHM-201-YS-01 | RL7-CHM-201-YS-01 |  |  | ROLL MACHINE OK TO RUN PERMISSIVE | DG6818 | CHILL | RL7-SERP-RIO1 | 15 | 6 | 0 | 24 VDC DO | 5069-OB16
50 | RL7-CHR-201-AH-01 | RL7-CHR-201-AH-01 |  |  | SERPENTINE ALARM HORN | DG6820 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 0 | 24 VDC DO | 5069-OB16
50 | RL7-GRR-103-ZSS-01 | RL7-GRR-103-ZSS-01 | BGZ01 | P002-JB01 | FROZEN BLOCK CRUSHER LEFT ACCESS DOOR 1 SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 1 | 0 | 24 VDC SI | 5069-IB8S
51 | RL7-GRR-103-ZSS-01 | RL7-GRR-103-ZSS-01 | BGZ01 | P002-JB01 | FROZEN BLOCK CRUSHER LEFT ACCESS DOOR 1 SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 1 | 1 | 24 VDC SI | 5069-IB8S
52 | RL7-GRR-103-ZSS-02 | RL7-GRR-103-ZSS-02 | BGZ02 | P002-JB01 | FROZEN BLOCK CRUSHER LEFT ACCESS DOOR 2 SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 1 | 2 | 24 VDC SI | 5069-IB8S
53 | RL7-GRR-103-ZSS-02 | RL7-GRR-103-ZSS-02 | BGZ02 | P002-JB01 | FROZEN BLOCK CRUSHER LEFT ACCESS DOOR 2 SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 1 | 3 | 24 VDC SI | 5069-IB8S
54 | RL7-GRR-103-ZSS-03 | RL7-GRR-103-ZSS-03 | BGZ03 | P002-JB01 | FROZEN BLOCK CRUSHER RIGHT ACCESS DOOR 1 SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 1 | 4 | 24 VDC SI | 5069-IB8S
55 | RL7-GRR-103-ZSS-03 | RL7-GRR-103-ZSS-03 | BGZ03 | P002-JB01 | FROZEN BLOCK CRUSHER RIGHT ACCESS DOOR 1 SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 1 | 5 | 24 VDC SI | 5069-IB8S
56 | RL7-GRR-103-ZSS-04 | RL7-GRR-103-ZSS-04 | BGZ04 | P002-JB01 | FROZEN BLOCK CRUSHER RIGHT ACCESS DOOR 2 SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 1 | 6 | 24 VDC SI | 5069-IB8S
57 | RL7-GRR-103-ZSS-04 | RL7-GRR-103-ZSS-04 | BGZ04 | P002-JB01 | FROZEN BLOCK CRUSHER RIGHT ACCESS DOOR 2 SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 1 | 7 | 24 VDC SI | 5069-IB8S
58 | RL7-CNV-109-ZSS-01 | RL7-CNV-109-ZSS-01 | BGZ01 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER LID 1 COVER SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 2 | 0 | 24 VDC SI | 5069-IB8S
59 | RL7-CNV-109-ZSS-01 | RL7-CNV-109-ZSS-01 | BGZ01 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER LID 1 COVER SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 2 | 1 | 24 VDC SI | 5069-IB8S
60 | RL7-CNV-109-ZSS-02 | RL7-CNV-109-ZSS-02 | BGZ02 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER LID 2 COVER SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 2 | 2 | 24 VDC SI | 5069-IB8S
61 | RL7-CNV-109-ZSS-02 | RL7-CNV-109-ZSS-02 | BGZ02 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER LID 2 COVER SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 2 | 3 | 24 VDC SI | 5069-IB8S
62 | RL7-CNV-109-ZSS-03 | RL7-CNV-109-ZSS-03 | BGZ03 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER LID 3 COVER SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 2 | 4 | 24 VDC SI | 5069-IB8S
63 | RL7-CNV-109-ZSS-03 | RL7-CNV-109-ZSS-03 | BGZ03 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER LID 3 COVER SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 2 | 5 | 24 VDC SI | 5069-IB8S
64 | RL7-CNV-109-ZSS-04 | RL7-CNV-109-ZSS-04 | BGZ04 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER LID 4 COVER SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 2 | 6 | 24 VDC SI | 5069-IB8S
65 | RL7-CNV-109-ZSS-04 | RL7-CNV-109-ZSS-04 | BGZ04 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER LID 4 COVER SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 2 | 7 | 24 VDC SI | 5069-IB8S
66 |  | RL7-CNV-109-ZSS-05 | BGZ05 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER LID 5 COVER SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 3 | 0 | 24 VDC SI | 5069-IB8S
67 |  | RL7-CNV-109-ZSS-05 | BGZ05 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER LID 5 COVER SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 3 | 1 | 24 VDC SI | 5069-IB8S
68 |  | RL7-CNV-109-ZSS-06 | BGZ06 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER BOMB DOOR 1 SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 3 | 2 | 24 VDC SI | 5069-IB8S
69 |  | RL7-CNV-109-ZSS-06 | BGZ06 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER BOMB DOOR 1 SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 3 | 3 | 24 VDC SI | 5069-IB8S
70 |  | RL7-CNV-109-ZSS-07 | BGZ07 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER BOMB DOOR 2 SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 3 | 4 | 24 VDC SI | 5069-IB8S
71 |  | RL7-CNV-109-ZSS-07 | BGZ07 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER BOMB DOOR 2 SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 3 | 5 | 24 VDC SI | 5069-IB8S
72 | RL7-CNV-109-ZSS-08 | RL7-CNV-109-ZSS-08 | BGZ08 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER INSPECTION DOOR SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 3 | 6 | 24 VDC SI | 5069-IB8S
73 | RL7-CNV-109-ZSS-08 | RL7-CNV-109-ZSS-08 | BGZ08 | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER INSPECTION DOOR SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 3 | 7 | 24 VDC SI | 5069-IB8S
74 | RL7-CNV-109-ZSS-09 | RL7-CNV-109-PB-01 |  | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER E-STOP PB SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 4 | 0 | 24 VDC SI | 5069-IB8S
75 | RL7-CNV-109-ZSS-09 | RL7-CNV-109-PB-01 |  | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER E-STOP PB SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 4 | 1 | 24 VDC SI | 5069-IB8S
76 | RL7-GRR-103-PB-01 | RL7-GRR-103-PB-01 |  | P003-JB01 | FROZEN BLOCK CRUSHER E-STOP PB SAFETY INPUT CH1 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 4 | 6 | 24 VDC SI | 5069-IB8S
77 | RL7-GRR-103-PB-01 | RL7-GRR-103-PB-01 |  | P003-JB01 | FROZEN BLOCK CRUSHER E-STOP PB SAFETY INPUT CH2 | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 4 | 7 | 24 VDC SI | 5069-IB8S
78 | RL7-WBU-101-YI-01 | RL7-GRR-103-PSL-01 | BPD01 | P002-JB04 | FROZEN BLOCK CRUSHER RINSE SYSTEM COMPRESSED AIR PRESSURE SWITCH LOW | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 6 | 0 | 24 VDC DI | 5069-IB16
79 | RL7-GRR-103-XV-00 | RL7-GRR-103-XV-00 | MB00 | P002-JB04 | FROZEN BLOCK CRUSHER RINSE SYSTEM ZONES 1 AND 2 VALVE ROTATION | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 8 | 1 | 24 VDC DO | 5069-OB16
80 | RL7-GRR-103-XV-01 | RL7-GRR-103-XV-01 | MB01 | P002-JB04 | FROZEN BLOCK CRUSHER RINSE SYSTEM ZONE 1 VALVE | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 8 | 2 | 24 VDC DO | 5069-OB16
81 | RL7-GRR-103-XV-02 | RL7-GRR-103-XV-02 | MB02 | P002-JB04 | FROZEN BLOCK CRUSHER RINSE SYSTEM ZONE 2 VALVE | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 8 | 3 | 24 VDC DO | 5069-OB16
82 | RL7-GRR-103-XV-03 | RL7-GRR-103-XV-03 | MB03 | P002-JB04 | FROZEN BLOCK CRUSHER RINSE SYSTEM ZONE 3 VALVE | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 8 | 4 | 24 VDC DO | 5069-OB16
83 | RL7-GRR-103-XV-04 | RL7-GRR-103-XV-04 | MB04 | P002-JB04 | FROZEN BLOCK CRUSHER RINSE SYSTEM ZONE 4 VALVE | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 8 | 5 | 24 VDC DO | 5069-OB16
84 | RL7-GRR-103-XV-05 | RL7-GRR-103-XV-05 | MB05 | P002-JB04 | FROZEN BLOCK CRUSHER RINSE SYSTEM ZONE 5 VALVE | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 8 | 6 | 24 VDC DO | 5069-OB16
85 | RL7-GRR-103-XV-06 | RL7-GRR-103-XV-06 | MB06 | P002-JB04 | FROZEN BLOCK CRUSHER RINSE SYSTEM ZONE 6 VALVE | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 8 | 7 | 24 VDC DO | 5069-OB16
86 | RL7-GRR-103-PBL-01 | RL7-GRR-103-PBL-01 |  | P002-JB01 | FROZEN BLOCK CRUSHER E-STOP PUSHBUTTON PILOT LIGHT | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 8 | 11 | 24 VDC DO | 5069-OB16
87 | RL7-CNV-109-PBL-01 | RL7-CNV-109-PBL-01 |  | P003-JB01 | FROZEN BLOCK CRUSHER INCLINE AUGER E-STOP PILOT LIGHT | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 8 | 15 | 24 VDC DO | 5069-OB16
88 | RL7-CNV-109-XV-01 | RL7-CNV-109-XV-01 | MB07 | P002-JB04 | FROZEN BLOCK CRUSHER INCLINE AUGER DRAIN VALVE | DG7000 | PROC | RL7-PBK-RIO1 | 1 | 9 | 1 | 24 VDC DO | 5069-OB16
90 | RL7-GRR-101-ZSS-04 | RL7-GRR-101-ZSS-04 | PRS2206021 | JIC22B | GRINDER ACCESS DOOR SAFETY INPUT CH1 | DG7000 | PROC | RL7-IPA2-RIO1 | 7 | 1 | 0 | 24 VDC SI | 5069-IB8S
91 | RL7-GRR-101-ZSS-04 | RL7-GRR-101-ZSS-04 | PRS2206021 | JIC22B | GRINDER ACCESS DOOR SAFETY INPUT CH2 | DG7000 | PROC | RL7-IPA2-RIO1 | 7 | 1 | 1 | 24 VDC SI | 5069-IB8S
92 | RL7-GRR-101-ZSS-01 | RL7-GRR-101-ZSS-01 | PRS2206061 | JIC22B | GRINDER HOPPER SAFETY INPUT CH1 | DG7000 | PROC | RL7-IPA2-RIO1 | 7 | 1 | 2 | 24 VDC SI | 5069-IB8S
93 | RL7-GRR-101-ZSS-01 | RL7-GRR-101-ZSS-01 | PRS2206061 | JIC22B | GRINDER HOPPER SAFETY INPUT CH2 | DG7000 | PROC | RL7-IPA2-RIO1 | 7 | 1 | 3 | 24 VDC SI | 5069-IB8S
94 | RL7-GRR-101-ZSS-02 | RL7-GRR-101-ZSS-02 | PRS2206101 | JIC22B | GRINDER PLATE GUARD SAFETY INPUT CH1 | DG7000 | PROC | RL7-IPA2-RIO1 | 7 | 1 | 4 | 24 VDC SI | 5069-IB8S
95 | RL7-GRR-101-ZSS-02 | RL7-GRR-101-ZSS-02 | PRS2206101 | JIC22B | GRINDER PLATE GUARD SAFETY INPUT CH2 | DG7000 | PROC | RL7-IPA2-RIO1 | 7 | 1 | 5 | 24 VDC SI | 5069-IB8S
96 | RL7-GRR-101-ZSS-03 | RL7-GRR-101-ZSS-03 | PRS2206161 | JIC22B | GRINDER DISCHARGE BELT CONVEYOR IN PLACE SAFETY INPUT CH1 | DG7000 | PROC | RL7-IPA2-RIO1 | 7 | 1 | 6 | 24 VDC SI | 5069-IB8S
97 | RL7-GRR-101-ZSS-03 | RL7-GRR-101-ZSS-03 | PRS2206161 | JIC22B | GRINDER DISCHARGE BELT CONVEYOR IN PLACE SAFETY INPUT CH1 | DG7000 | PROC | RL7-IPA2-RIO1 | 7 | 1 | 7 | 24 VDC SI | 5069-IB8S
98 | RL7-GRR-101-PB-01 | RL7-GRR-101-PB-01 |  |  | GRINDER PLATFORM E-STOP PUSHBUTTON SAFETY INPUT CH1 | DG7000 | PROC | RL7-IPA2-RIO1 | 7 | 2 | 0 | 24 VDC SI | 5069-IB8S
99 | RL7-GRR-101-PB-01 | RL7-GRR-101-PB-01 |  |  | GRINDER PLATFORM E-STOP PUSHBUTTON SAFETY INPUT CH2 | DG7000 | PROC | RL7-IPA2-RIO1 | 7 | 2 | 1 | 24 VDC SI | 5069-IB8S
99 |  | RL7-CNV-111-ZSO-01 | PRS1505111 |  | SURGE BIN 1 DIVERTER GATE EXTENDED | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 3 | 0 | 24 VDC DI | 5069-IB8S
100 |  | RL7-CNV-111-ZSC-01 | PRS1505131 |  | SURGE BIN 1 DIVERTER GATE RETRACTED | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 3 | 1 | 24 VDC DI | 5069-IB8S
101 |  | RL7-CNV-111-ZSO-02 | PRS1505151 |  | SURGE BIN 2 DIVERTER GATE EXTENDED | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 3 | 2 | 24 VDC DI | 5069-IB8S
102 |  | RL7-CNV-111-ZSC-02 | PRS1505171 |  | SURGE BIN 2 DIVERTER GATE RETRACTED | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 3 | 3 | 24 VDC DI | 5069-IB8S
103 |  | RL7-CNV-111-ZSO-03 | PRS1505191 |  | SURGE BIN 3 DIVERTER GATE EXTENDED | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 3 | 4 | 24 VDC DI | 5069-IB8S
104 |  | RL7-CNV-111-ZSC-03 | PRS1505211 |  | SURGE BIN 3 DIVERTER GATE RETRACTED | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 3 | 5 | 24 VDC DI | 5069-IB8S
105 |  | RL7-CNV-111-ZSO-04 | PRS1505131 |  | SURGE BIN 4 DIVERTER GATE EXTENDED | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 3 | 6 | 24 VDC DI | 5069-IB8S
106 |  | RL7-CNV-111-ZSC-04 | PRS1505151 |  | SURGE BIN 4 DIVERTER GATE RETRACTED | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 3 | 7 | 24 VDC DI | 5069-IB8S
107 |  | RL7-CNV-111-PSL-01 | PRG1505011 |  | SURGE BIN DIVERTERS LOW PNEUMATIC PRESSURE | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 3 | 8 | 24 VDC DI | 5069-IB8S
108 |  | RL7-CNV-110-PSL-01 | PRG1405011 |  | METAL DETECTOR CONVEYOR PULL NOSE PNUEMATIC PRESSURE SWITCH | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 3 | 9 | 24 VDC DI | 5069-IB8S
109 |  | RL7-CNV-111-XY-01A | SOL1505031 |  | DIVERTER GATE 1 SOLENOID EXTEND | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 0 | 24 VDC DO | 5069-ARM
110 |  | RL7-CNV-111-XY-01B | SOL1505031 |  | DIVERTER GATE 1 SOLENOID RETRACT | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 1 | 24 VDC DO | 5069-IB16
111 |  | RL7-CNV-111-XY-02A | SOL1505061 |  | DIVERTER GATE 2 SOLENOID EXTEND | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 2 | 24 VDC DO | 5069-IB16
112 |  | RL7-CNV-111-XY-02B | SOL1505061 |  | DIVERTER GATE 2 SOLENOID RETRACT | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 3 | 24 VDC DO | 5069-IB16
113 |  | RL7-CNV-111-XY-03A | SOL1505081 |  | DIVERTER GATE 3 SOLENOID EXTEND | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 4 | 24 VDC DO | 5069-IB16
114 |  | RL7-CNV-111-XY-03B | SOL1505081 |  | DIVERTER GATE 3 SOLENOID RETRACT | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 5 | 24 VDC DO | 5069-IB16
115 |  | RL7-CNV-111-XY-04A | SOL1505101 |  | DIVERTER GATE 4 SOLENOID EXTEND | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 6 | 24 VDC DO | 5069-IB16
116 |  | RL7-CNV-111-XY-04B | SOL1505101 |  | DIVERTER GATE 4 SOLENOID RETRACT | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 7 | 24 VDC DO | 5069-IB16
117 |  | RL7-CNV-110-XY-01A | SOL1405031 |  | METAL DETECTOR CONVEYOR PULL NOSE EXTEND | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 8 | 24 VDC DO | 5069-ARM
118 |  | RL7-CNV-110-XY-01B | SOL1405031 |  | METAL DETECTOR CONVEYOR PULL NOSE RETRACT | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 9 | 24 VDC DO | 5069-IB16
119 |  | RL7-CNV-111-XV-05 |  |  | SURGE BIN SUPPLY CONVEYOR SANITATION VALVE OPEN SOLENOID | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 10 | 24 VDC DO | 5069-IB16
120 |  | RL7-CNV-110-XY-02 |  |  | METAL DETECTOR CONVEYOR SANITATION VALVE OPEN SOLNOID | DG7001 | PROC | RL7-BINS-RIO1 | 3 | 4 | 11 | 24 VDC DO | 5069-IB16
121 | RL7-BIN-101-ZSS-01 | RL7-BIN-101-ZSS-01 | PRS1605021 |  | SURGE BIN 1 DISCHARGE TROUGH COVER SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 1 | 0 | 24 VDC SI | 5069-IB8S
122 | RL7-BIN-101-ZSS-01 | RL7-BIN-101-ZSS-01 | PRS1605021 |  | SURGE BIN 1 DISCHARGE TROUGH COVER SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 1 | 1 | 24 VDC SI | 5069-IB8S
123 | RL7-BIN-101-ZSS-02 | RL7-BIN-101-ZSS-02 | PRS1605061 |  | SURGE BIN 1 DISCHARGE SANITATION DOOR SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 1 | 2 | 24 VDC SI | 5069-IB8S
124 | RL7-BIN-101-ZSS-02 | RL7-BIN-101-ZSS-02 | PRS1605061 |  | SURGE BIN 1 DISCHARGE SANITATION DOOR SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 1 | 3 | 24 VDC SI | 5069-IB8S
125 | RL7-BIN-102-ZSS-01 | RL7-BIN-102-ZSS-01 | PRS1705021 |  | SURGE BIN 2 DISCHARGE TROUGH COVER SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 1 | 4 | 24 VDC SI | 5069-IB8S
126 | RL7-BIN-102-ZSS-01 | RL7-BIN-102-ZSS-01 | PRS1705021 |  | SURGE BIN 2 DISCHARGE TROUGH COVER SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 1 | 5 | 24 VDC SI | 5069-IB8S
127 | RL7-BIN-102-ZSS-02 | RL7-BIN-102-ZSS-02 | PRS1705061 |  | SURGE BIN 2 DISCHARGE SANITATION DOOR SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 1 | 6 | 24 VDC SI | 5069-IB8S
128 | RL7-BIN-102-ZSS-02 | RL7-BIN-102-ZSS-02 | PRS1705061 |  | SURGE BIN 2 DISCHARGE SANITATION DOOR SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 1 | 7 | 24 VDC SI | 5069-IB8S
129 | RL7-BIN-101-ZSS-03 | RL7-BIN-101-ZSS-03 | PRS1605161 |  | SURGE BIN 1 SANITATION ACCESS GATE SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 2 | 0 | 24 VDC SI | 5069-IB8S
130 | RL7-BIN-101-ZSS-03 | RL7-BIN-101-ZSS-03 | PRS1605161 |  | SURGE BIN 1 SANITATION ACCESS GATE SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 2 | 1 | 24 VDC SI | 5069-IB8S
131 | RL7-BIN-101-PB-01 | RL7-BIN-102-ZSS-03 | PRS1605201 |  | SURGE BIN 2 SANITATION ACCESS GATE SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 2 | 2 | 24 VDC SI | 5069-IB8S
132 | RL7-BIN-101-PB-01 | RL7-BIN-102-ZSS-03 | PRS1605201 |  | SURGE BIN 2 SANITATION ACCESS GATE SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 2 | 3 | 24 VDC SI | 5069-IB8S
133 |  | RL7-BIN-101-PB-01 |  |  | SURGE BINS NORTH E-STOP PUSHBUTTON SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 2 | 4 | 24 VDC SI | 5069-IB8S
134 |  | RL7-BIN-101-PB-01 |  |  | SURGE BINS NORTH E-STOP PUSHBUTTON SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 2 | 5 | 24 VDC SI | 5069-IB8S
135 | RL7-CNV-111-PSL-01 | RL7-BIN-101-PBL-01 |  |  | SURGE BINS NORTH E-STOP PUSHBUTTON PILOT LIGHT | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 6 | 0 | 24 VDC DO | 5069-IB16
136 | RL7-CNV-110-ZSO-01 | RL7-BIN-101-XY-01 |  |  | SURGE BIN 1 SANITATION VALVE OPEN SOLENOID | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 6 | 1 | 24 VDC DO | 5069-IB16
137 | RL7-CNV-110-ZSC-01 | RL7-BIN-102-XY-01 |  |  | SURGE BIN 2 SANITATION VALVE OPEN SOLENOID | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 6 | 2 | 24 VDC DO | 5069-IB16
138 | RL7-CNV-110-PSL-01 | RL7-BIN-102-AH-02 |  |  | SURGE BIN 2 ALARM HORN | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 6 | 3 | 24 VDC DO | 5069-IB16
139 | RL7-CNV-110-ZSO-02 | RL7-BIN-102-PL-01R |  |  | SURGE BIN 2 RED PILOT LIGHT | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 6 | 4 | 24 VDC DO | 5069-IB16
140 | RL7-CNV-110-ZSC-02 | RL7-BIN-102-PL-01Y |  |  | SURGE BIN 2 YELLOW PILOT LIGHT | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 6 | 5 | 24 VDC DO | 5069-IB16
141 | RL7-CNV-111-ZSO-05 | RL7-BIN-102-PL-01G |  |  | SURGE BIN 2 GREEN PILOT LIGHT | DG7002 | PROC | RL7-BINA-RIO1 | 4 | 6 | 6 | 24 VDC DO | 5069-IB16
142 | RL7-BIN-103-ZSS-01 | RL7-BIN-103-ZSS-01 | PRS1805021 | JIC19B | SURGE BIN 3 DISCHARGE TROUGH COVER SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 1 | 0 | 24 VDC SI | 5069-IB8S
143 | RL7-BIN-103-ZSS-01 | RL7-BIN-103-ZSS-01 | PRS1805021 | JIC19B | SURGE BIN 3 DISCHARGE TROUGH COVER SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 1 | 1 | 24 VDC SI | 5069-IB8S
144 | RL7-BIN-103-ZSS-02 | RL7-BIN-103-ZSS-02 | PRS1805061 | JIC19B | SURGE BIN 3 DISCHARGE SANITATION DOOR SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 1 | 2 | 24 VDC SI | 5069-IB8S
145 | RL7-BIN-103-ZSS-02 | RL7-BIN-103-ZSS-02 | PRS1805061 | JIC19B | SURGE BIN 3 DISCHARGE SANITATION DOOR SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 1 | 3 | 24 VDC SI | 5069-IB8S
146 | RL7-BIN-104-ZSS-01 | RL7-BIN-104-ZSS-01 | PRS1905021 | JIC19B | SURGE BIN 4 DISCHARGE TROUGH COVER SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 1 | 4 | 24 VDC SI | 5069-IB8S
147 | RL7-BIN-104-ZSS-01 | RL7-BIN-104-ZSS-01 | PRS1905021 | JIC19B | SURGE BIN 4 DISCHARGE TROUGH COVER SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 1 | 5 | 24 VDC SI | 5069-IB8S
148 | RL7-BIN-104-ZSS-02 | RL7-BIN-104-ZSS-02 | PRS1905061 | JIC19B | SURGE BIN 4 DISCHARGE SANITATION DOOR SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 1 | 6 | 24 VDC SI | 5069-IB8S
149 | RL7-BIN-104-ZSS-02 | RL7-BIN-104-ZSS-02 | PRS1905061 | JIC19B | SURGE BIN 4 DISCHARGE SANITATION DOOR SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 1 | 7 | 24 VDC SI | 5069-IB8S
150 | RL7-BIN-103-ZSS-03 | RL7-BIN-103-ZSS-03 | PRS1905161 | JIC19B | SURGE BIN 3 SANITATION ACCESS GATE SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 2 | 0 | 24 VDC SI | 5069-IB8S
151 | RL7-BIN-103-ZSS-03 | RL7-BIN-103-ZSS-03 | PRS1905161 | JIC19B | SURGE BIN 3 SANITATION ACCESS GATE SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 2 | 1 | 24 VDC SI | 5069-IB8S
152 | RL7-BIN-104-PB-01 | RL7-BIN-104-ZSS-03 | PRS1905201 | JIC19B | SURGE BIN 4 SANITATION ACCESS GATE SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 2 | 2 | 24 VDC SI | 5069-IB8S
153 | RL7-BIN-104-PB-01 | RL7-BIN-104-ZSS-03 | PRS1905201 | JIC19B | SURGE BIN 4 SANITATION ACCESS GATE SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 2 | 3 | 24 VDC SI | 5069-IB8S
154 | RL7-CNV-114-ZSS-05 | RL7-CNV-112-PB-01 |  |  | SURGE BIN TAKEAWAY CONVEYOR E-STOP PUSHBUTTON SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 2 | 4 | 24 VDC SI | 5069-IB8S
155 | RL7-CNV-114-ZSS-05 | RL7-CNV-112-PB-01 |  |  | SURGE BIN TAKEAWAY CONVEYOR E-STOP PUSHBUTTON SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 2 | 5 | 24 VDC SI | 5069-IB8S
156 | RL7-BIN-104-ZSS-03 | RL7-BIN-104-PB-01 |  |  | SURGE BIN SOUTH E-STOP PUSHBUTTON SAFETY INPUT CH1 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 2 | 6 | 24 VDC SI | 5069-IB8S
157 | RL7-BIN-104-ZSS-03 | RL7-BIN-104-PB-01 |  |  | SURGE BIN SOUTH E-STOP PUSHBUTTON SAFETY INPUT CH2 | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 2 | 7 | 24 VDC SI | 5069-IB8S
158 | RL7-CNV-114-ZSC-06 | RL7-BIN-104-PBL-01 |  |  | SURGE BIN SOUTH E-STOP PUSHBUTTON PILOT LIGHT | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 6 | 0 | 24 VDC DO | 5069-IB16
159 | RL7-CNV-114-ZSC-05 | RL7-CNV-112-PBL-01 |  |  | SURGE BIN TAKEAWAY CONVEYOR E-STOP PUSHBUTTON PILOT LIGHT | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 6 | 1 | 24 VDC DO | 5069-IB16
160 | RL7-CNV-114-ZSC-01 | RL7-CNV-112-XY-01 |  |  | SURGE BIN TAKEAWAY CONVEYOR SANITATION VALVE OPEN SOLENOID | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 6 | 2 | 24 VDC DO | 5069-IB16
161 | RL7-CNV-114-ZSC-02 | RL7-BIN-103-XY-01 |  |  | SURGE BIN 3 SANITATION VALVE OPEN SOLENOID | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 6 | 3 | 24 VDC DO | 5069-IB16
162 | RL7-CNV-114-ZSC-04 | RL7-BIN-104-XY-01 |  |  | SURGE BIN 4 SANITATION VALVE OPEN SOLENOID | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 6 | 4 | 24 VDC DO | 5069-IB16
163 | RL7-CNV-114-ZSC-03 | RL7-BIN-104-AH-01 |  |  | SURGE BIN 4 ALARM HORN | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 6 | 5 | 24 VDC DO | 5069-IB16
164 | RL7-BIN-103-ZSO-01 | RL7-BIN-104-PL-01R |  |  | SURGE BIN 4 RED PILOT LIGHT | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 6 | 6 | 24 VDC DO | 5069-IB16
165 | RL7-BIN-103-ZSC-01 | RL7-BIN-104-PL-01Y |  |  | SURGE BIN 4 YELLOW PILOT LIGHT | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 6 | 7 | 24 VDC DO | 5069-IB16
166 |  | RL7-BIN-104-PL-01G |  |  | SURGE BIN 4 GREEN PILOT LIGHT | DG7002 | PROC | RL7-BINB-RIO1 | 5 | 6 | 8 | 24 VDC DO | 5069-IB16
168 | RL7-BIN-103-ZSS-01 | RL7-CNV-114-ZSS-04 | PRS2106021 | JIC21B | INCLINE PIVOT AUGER 1 TROUGH COVER 1 SAFETY INPUT CH1 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 1 | 0 | 24 VDC SI | 5069-IB8S
169 | RL7-BIN-103-ZSS-01 | RL7-CNV-114-ZSS-04 | PRS2106021 | JIC21B | INCLINE PIVOT AUGER 1 TROUGH COVER 1 SAFETY INPUT CH2 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 1 | 1 | 24 VDC SI | 5069-IB8S
170 | RL7-BIN-103-ZSS-02 | RL7-CNV-114-ZSS-01 | PRS2106101 | JIC21B | INCLINE PIVOT AUGER 1 MAIN GUARD 1 SAFETY INPUT CH1 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 1 | 2 | 24 VDC SI | 5069-IB8S
171 | RL7-BIN-103-ZSS-02 | RL7-CNV-114-ZSS-01 | PRS2106101 | JIC21B | INCLINE PIVOT AUGER 1 MAIN GUARD 1 SAFETY INPUT CH2 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 1 | 3 | 24 VDC SI | 5069-IB8S
172 | RL7-BIN-104-ZSS-01 | RL7-CNV-114-ZSS-02 | PRS2106161 | JIC21B | INCLINE PIVOT AUGER 1 MAIN GUARD 2 SAFETY INPUT CH1 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 1 | 4 | 24 VDC SI | 5069-IB8S
173 | RL7-BIN-104-ZSS-01 | RL7-CNV-114-ZSS-02 | PRS2106161 | JIC21B | INCLINE PIVOT AUGER 1 MAIN GUARD 2 SAFETY INPUT CH2 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 1 | 5 | 24 VDC SI | 5069-IB8S
174 | RL7-BIN-104-ZSS-02 | RL7-CNV-114-ZSS-03 | PRS2106201 | JIC21B | INCLINE PIVOT AUGER 1 HOPPER SANITATION GUARD SAFETY INPUT CH1 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 1 | 6 | 24 VDC SI | 5069-IB8S
175 | RL7-BIN-104-ZSS-02 | RL7-CNV-114-ZSS-03 | PRS2106201 | JIC21B | INCLINE PIVOT AUGER 1 HOPPER SANITATION GUARD SAFETY INPUT CH2 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 1 | 7 | 24 VDC SI | 5069-IB8S
176 | RL7-BIN-103-ZSS-03 | RL7-CNV-114-ZSS-05 | PRS2106061 | JIC21B | INCLINE PIVOT AUGER 1 TROUGH COVER 2 SAFETY INPUT CH1 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 2 | 0 | 24 VDC SI | 5069-IB8S
177 | RL7-BIN-103-ZSS-03 | RL7-CNV-114-ZSS-05 | PRS2106061 | JIC21B | INCLINE PIVOT AUGER 1 TROUGH COVER 2 SAFETY INPUT CH2 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 2 | 1 | 24 VDC SI | 5069-IB8S
178 | RL7-BIN-104-PB-01 | RL7-CNV-113-ZSS-01 | PRS2106241 |  | INCLINE BELT CONVEYOR CHUTE IN PLACE SAFETY INPUT CH1 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 2 | 2 | 24 VDC SI | 5069-IB8S
179 | RL7-BIN-104-PB-01 | RL7-CNV-113-ZSS-01 | PRS2106241 |  | INCLINE BELT CONVEYOR CHUTE IN PLACE SAFETY INPUT CH2 | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 2 | 3 | 24 VDC SI | 5069-IB8S
180 |  | RL7-CNV-114-ZSC-06 | PRS2107231 | JIC21B | INCLINE PIVOT AUGER 1 PUMP COVER IS ON | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 4 | 0 | 24 VDC DI | 5069-IB8S
181 |  | RL7-CNV-114-ZSC-05 | PRS2107251 | JIC21B | INCLINE PIVOT AUGER 1 IN DOWN POSITION | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 4 | 1 | 24 VDC DI | 5069-IB8S
182 | RL7-CNV-113-ZSS-01 | RL7-CNV-114-ZSC-01 | PRS2107211 | JIC21B | INCLINE PIVOT AUGER 1 IN UP POSITION | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 4 | 2 | 24 VDC DI | 5069-IB8S
183 | RL7-CNV-113-ZSS-01 | RL7-CNV-114-ZSC-02 | PRS2107151 | JIC21B | INCLINE PIVOT AUGER 1 IN GRINDER RUN POSITION | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 4 | 3 | 24 VDC DI | 5069-IB8S
184 | RL7-CNV-112-PB-01 | RL7-CNV-114-ZSC-04 | PRS2107171 | JIC21B | INCLINE PIVOT AUGER 1 IN GRINDER BYPASS POSITION | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 4 | 4 | 24 VDC DI | 5069-IB8S
185 | RL7-CNV-112-PB-01 | RL7-CNV-114-ZSC-03 | PRS2107191 | JIC21B | INCLINE PIVOT AUGER 1 IN SANITATION POSITION | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 4 | 5 | 24 VDC DI | 5069-IB8S
186 | RL7-CNV-114-ZSC-06 | RL7-CNV-114-XY-101 | SOL2107121 | JIC21B | PIVOT INCLINE SCREW CONVEYOR 1 RAISE CONVEYOR SOLENOID | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 6 | 0 | 24 VDC DO | 5069-IB16
187 | RL7-CNV-114-ZSC-05 | RL7-CNV-114-XY-102 | SOL2107141 | JIC21B | PIVOT INCLINE SCREW CONVEYOR 1 LOWER CONVEYOR SOLENOID | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 6 | 1 | 24 VDC DO | 5069-IB16
188 | RL7-CNV-114-ZSC-01 | RL7-CNV-113-XY-01 |  |  | INCLINE BELT CONVEYOR 1 SANITATION VALVE OPEN SOLENOID | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 6 | 2 | 24 VDC DO | 5069-IB16
189 | RL7-CNV-114-ZSC-02 | RL7-CNV-114-XY-08 |  |  | INCLINE PIVOT AUGER 1 SANITATION VALVE OPEN SOLENOID | DG7003 | PROC | RL7-IPA1-RIO1 | 6 | 6 | 3 | 24 VDC DO | 5069-IB16
190 |  | RL7-CNV-114.M2 |  |  | INCLINE PIVOT AUGER 1 HYDRAULIC PUMP ENABLE | DG7003 | MCC | RL7-INTSL-RIO1 | 18 | 14 | 5 | 24 VDC DO | 5069-OB16
191 | RL7-CNV-115-ZSS-01 | RL7-CNV-115-ZSS-01 | PRS2305021 | JIC22B, JIC23B | INCLINE BELT CONVEYOR 2 CHUTE IN PLACE SAFETY INPUT CH1 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 2 | 2 | 24 VDC SI | 5069-IB8S
192 | RL7-CNV-115-ZSS-01 | RL7-CNV-115-ZSS-01 | PRS2305021 | JIC22B, JIC23B | INCLINE BELT CONVEYOR 2 CHUTE IN PLACE SAFETY INPUT CH1 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 2 | 3 | 24 VDC SI | 5069-IB8S
193 | RL7-CNV-115-PB-01 | RL7-CNV-115-PB-01 |  |  | INCLINE BELT CONVEYOR (TO PIVOT AUGER 2) E-STOP PUSHBUTTON SAFETY INPUT CH1 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 2 | 4 | 24 VDC SI | 5069-IB8S
194 | RL7-CNV-115-PB-01 | RL7-CNV-115-PB-01 |  |  | INCLINE BELT CONVEYOR (TO PIVOT AUGER 2) E-STOP PUSHBUTTON SAFETY INPUT CH2 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 2 | 5 | 24 VDC SI | 5069-IB8S
195 | RL7-CNV-106-ZSS-04 | RL7-CNV-106-ZSS-04 | PRS2406021 | JIC1B | INCLINE PIVOT AUGER 2 TROUGH COVER 1 SAFETY INPUT CH1 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 3 | 0 | 24 VDC SI | 5069-IB8S
196 | RL7-CNV-106-ZSS-04 | RL7-CNV-106-ZSS-04 | PRS2406021 | JIC1B | INCLINE PIVOT AUGER 2 TROUGH COVER 1 SAFETY INPUT CH2 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 3 | 1 | 24 VDC SI | 5069-IB8S
197 | RL7-CNV-106-ZSS-01 | RL7-CNV-106-ZSS-01 | PRS2406101 | JIC1B | INCLINE PIVOT AUGER 2 MAIN GUARD 1 SAFETY INPUT CH1 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 3 | 2 | 24 VDC SI | 5069-IB8S
198 | RL7-CNV-106-ZSS-01 | RL7-CNV-106-ZSS-01 | PRS2406101 | JIC1B | INCLINE PIVOT AUGER 2 MAIN GUARD 1 SAFETY INPUT CH2 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 3 | 3 | 24 VDC SI | 5069-IB8S
199 | RL7-CNV-106-ZSS-02 | RL7-CNV-106-ZSS-02 | PRS2406161 | JIC1B | INCLINE PIVOT AUGER 2 MAIN GUARD 2 SAFETY INPUT CH1 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 3 | 4 | 24 VDC SI | 5069-IB8S
200 | RL7-CNV-106-ZSS-02 | RL7-CNV-106-ZSS-02 | PRS2406161 | JIC1B | INCLINE PIVOT AUGER 2 MAIN GUARD 2 SAFETY INPUT CH2 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 3 | 5 | 24 VDC SI | 5069-IB8S
201 | RL7-CNV-106-ZSS-03 | RL7-CNV-106-ZSS-03 | PRS2406201 | JIC1B | INCLINE PIVOT AUGER 2 HOPPER SANITATION GUARD SAFETY CH1 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 3 | 6 | 24 VDC SI | 5069-IB8S
202 | RL7-CNV-106-ZSS-03 | RL7-CNV-106-ZSS-03 | PRS2406201 | JIC1B | INCLINE PIVOT AUGER 2 HOPPER SANITATION GUARD SAFETY CH2 | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 3 | 7 | 24 VDC SI | 5069-IB8S
203 | RL7-CNV-106-ZSC-06 | RL7-CNV-106-ZSC-06 |  | JIC1B | INCLINE PIVOT AUGER 2 PUMP COVER ON | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 6 | 0 | 24 VDC DI | 5069-IB16
204 | RL7-CNV-106-ZSC-03 | RL7-CNV-106-ZSC-03 | PRS247231 | JIC1B | INCLINE PIVOT AUGER 2 IN SANITATION POSITION | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 6 | 1 | 24 VDC DI | 5069-IB16
205 | RL7-CNV-106-ZSC-05 | RL7-CNV-106-ZSC-05 | PRS247251 | JIC1B | INCLINE PIVOT AUGER 2 IN DOWN POSITION | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 6 | 2 | 24 VDC DI | 5069-IB16
206 | RL7-CNV-106-ZSC-04 | RL7-CNV-106-ZSC-04 | PRS2407211 | JIC1B | INCLINE PIVOT AUGER 2 AT PRE-MIXER POSITION | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 6 | 3 | 24 VDC DI | 5069-IB16
207 | RL7-CNV-106-ZSC-01 | RL7-CNV-106-ZSC-01 | PRS2407191 | JIC1B | INCLINE PIVOT AUGER 2 IN UP POSITION | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 6 | 4 | 24 VDC DI | 5069-IB16
208 | RL7-CNV-106-ZSC-02 | RL7-CNV-106-ZSC-02 | PRS2407151 | JIC1B | INCLINE PIVOT AUGER 2 AT GRINDER POSITION | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 6 | 5 | 24 VDC DI | 5069-IB16 | [11 empty] | NOT IN PH2 DWGS?
209 | RL7-GRR-101-LSL-01 | RL7-GRR-101-LSL-01 |  |  | GRINDER LEVEL SWITCH LOW | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 6 | 6 | 24 VDC DI | 5069-IB16
210 | RL7-GRR-101-LSH-01 | RL7-GRR-101-LSH-01 |  |  | GRINDER LEVEL SWITCH HIGH | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 6 | 7 | 24 VDC DI | 5069-IB16
211 | RL7-CNV-106-XY-101 | RL7-CNV-106-XY-101 | SOL2407121 | JIC1B | INCLINE PIVOT AUGER 2 RAISE SOLENOID | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 7 | 2 | 24 VDC DO | 5069-OB16
212 | RL7-CNV-106-XY-102 | RL7-CNV-106-XY-102 | SOL2407141 | JIC1B | INCLINE PIVOT AUGER 2 LOWER SOLENOID | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 7 | 3 | 24 VDC DO | 5069-OB16
213 |  | RL7-CNV-106-XY-08 |  |  | INCLINE PIVOT AUGER 2 SANITATION VALVE OPEN SOLENOID | DG7004 | PROC | RL7-IPA2-RIO1 | 7 | 7 | 4 | 24 VDC DO | 5069-OB16
214 |  | RL7-GRR-101.M1 |  |  | GRINDER MOTOR ENABLE | DG7004 | MCC | RL7-INTSL-RIO1 | 18 | 14 | 4 | 24 VDC DO | 5069-OB16
215 |  | RL7-CNV-106.M2 |  |  | INCLINE PIVOT AUGER 2 HYDRAULIC PUMP ENABLE | DG7004 | MCC | RL7-INTSL-RIO1 | 18 | 14 | 6 | 24 VDC DO | 5069-OB16
216 | RL7-TNK-101-PB-01 | RL7-TNK-101-PB-01 |  |  | BREDDO MIXER E-STOP PB SAFETY INPUT CH1 | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 1 | 0 | 24 VDC SI | 5069-IB8S
217 | RL7-TNK-101-PB-01 | RL7-TNK-101-PB-01 |  |  | BREDDO MIXER E-STOP PB SAFETY INPUT CH2 | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 1 | 1 | 24 VDC SI | 5069-IB8S
218 | RL7-DRM-101-PB-01 | RL7-DRM-101-PB-01 | ESTOP111 |  | BREDDO DUMPER E-STOP PB SAFETY INPUT CH1 | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 1 | 2 | 24 VDC SI | 5069-IB8S
219 | RL7-DRM-101-PB-01 | RL7-DRM-101-PB-01 | ESTOP111 |  | BREDDO DUMPER E-STOP PB SAFETY INPUT CH2 | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 1 | 3 | 24 VDC SI | 5069-IB8S
220 | RL7-DRM-101-ZSS-01 | RL7-DRM-101-ZSS-01 | DV121B |  | BREDDO DUMPER LIGHT CURTAIN SAFETY INPUT CH1 | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 1 | 4 | 24 VDC SI | 5069-IB8S
221 | RL7-DRM-101-ZSS-01 | RL7-DRM-101-ZSS-01 | DV121B |  | BREDDO DUMPER LIGHT CURTAIN SAFETY INPUT CH2 | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 1 | 5 | 24 VDC SI | 5069-IB8S
222 | RL7-TNK-101-ZSO-01 | RL7-TNK-101-ZSO-01 |  |  | BREDDO MIXER PCW SUPPLY VALVE OPEN LIMIT SWITCH | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 3 | 0 | 24 VDC DI | 5069-IB16
223 | RL7-TNK-101-ZSC-01 | RL7-TNK-101-ZSC-01 |  |  | BREDDO MIXER PCW SUPPLY VALVE CLOSED LIMIT SWITCH | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 3 | 1 | 24 VDC DI | 5069-IB16
224 | RL7-TNK-101-ZSO-02 | RL7-TNK-101-ZSO-02 |  |  | BREDDO MIXER CIP / PCW MIX PROOF VALVE PCW LIMIT SWITCH | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 3 | 2 | 24 VDC DI | 5069-IB16
225 | RL7-TNK-101-ZSC-02 | RL7-TNK-101-ZSC-02 |  |  | BREDDO MIXER CIP / PCW MIX PROOF VALVE CIP LIMIT SWITCH | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 3 | 3 | 24 VDC DI | 5069-IB16
226 | RL7-TNK-101-ZSO-03 | RL7-TNK-101-ZSO-03 |  |  | BREDDO MIXER DISCHARGE VALVE OPEN LIMIT SWITCH | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 3 | 4 | 24 VDC DI | 5069-IB16
227 | RL7-TNK-101-ZSC-03 | RL7-TNK-101-ZSC-03 |  |  | BREDDO MIXER DISCHARGE VALVE CLOSED LIMIT SWITCH | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 3 | 5 | 24 VDC DI | 5069-IB16
228 | RL7-SKD-101-ZSO-01 | RL7-SKD-101-ZSO-01 |  |  | BREDDO FILTER GUM SUPPLY VALVE OPEN LIMIT SWITCH | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 3 | 8 | 24 VDC DI | 5069-IB16
229 | RL7-SKD-101-ZSC-01 | RL7-SKD-101-ZSC-01 |  |  | BREDDO FILTER GUM SUPPLY VALVE CLOSED LIMIT SWITCH | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 3 | 9 | 24 VDC DI | 5069-IB16
230 | RL7-DRM-101-PB-02 | RL7-DRM-101-PB-02 | PB114 |  | BREDDO DUMPER LIGHT CURTAIN RESET PUSHBUTTON | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 3 | 10 | 24 VDC DI | 5069-IB16
231 | RL7-DRM-101-PB-03 | RL7-DRM-101-PB-03 | PB116 |  | BREDDO DUMPER QR SCAN ENABLE PUSHBUTTON | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 3 | 11 | 24 VDC DI | 5069-IB16
232 | RL7-DRM-101-PSL-01 | RL7-DRM-101-PSL-01 | PS201 |  | BREDDO SYSTEM COMPRESSED AIR LOW PRESSURE SWITCH | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 4 | 5 | 24 VDC DI | 5069-IB16
233 |  | RL7-DRM-101-PSL-02 | PS203 |  | BREDDO DUMPER SEAL PRESSURE SWITCH | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 4 | 6 | 24 VDC DI | 5069-IB16
234 | RL7-DRM-101-ZSC-06 | RL7-DRM-101-ZSC-06 | PRS205 |  | BREDDO DUMPER UNSEAL PROX | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 4 | 7 | 24 VDC DI | 5069-IB16
235 | RL7-DRM-101-ZSC-07 | RL7-DRM-101-ZSC-07 | PRS207 |  | BREDDO DUMPER PIVOT PROX | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 4 | 8 | 24 VDC DI | 5069-IB16
236 | RL7-DRM-101-ZSC-08 | RL7-DRM-101-ZSC-08 | PRS209 |  | BREDDO DUMPER REVERSE PIVOT PROX | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 4 | 9 | 24 VDC DI | 5069-IB16
237 | RL7-DRM-101-ZSC-09 | RL7-DRM-101-ZSC-09 | PRS214 |  | BREDDO DUMPER PIVOT SLOW SPEED PROX | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 4 | 10 | 24 VDC DI | 5069-IB16
238 | RL7-DRM-101-ZSC-10 | RL7-DRM-101-ZSC-10 | PRS216 |  | BREDDO DUMPER REVERSE PIVOT SLOW SPEED PROX | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 4 | 11 | 24 VDC DI | 5069-IB16
239 | RL7-DRM-101-ZSC-11 | RL7-DRM-101-ZSC-11 | PEC218 |  | BREDDO DUMPER CONTAINER IN PLACE PROX | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 4 | 12 | 24 VDC DI | 5069-IB16
240 | RL7-TNK-101-PBL-01 | RL7-TNK-101-PBL-01 |  |  | BREDDO MIXER E-STOP PB PILOT LIGHT | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 6 | 0 | 24 VDC DO | 5069-OB16
241 | RL7-TNK-101-XY-02 | RL7-TNK-101-XV-02 |  |  | BREDDO MIXER CIP / PCW MIX PROOF VALVE OPEN SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 6 | 1 | 24 VDC DO | 5069-OB16
242 | RL7-TNK-101-XV-01 | RL7-TNK-101-XV-01 |  |  | BREDDO MIXER PCW SUPPLY VALVE OPEN SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 6 | 2 | 24 VDC DO | 5069-OB16
243 | RL7-TNK-101-XY-03 | RL7-TNK-101-XV-03 |  |  | BREDDO MIXER DISCHARGE VALVE OPEN SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 6 | 3 | 24 VDC DO | 5069-OB16
244 | RL7-TNK-101-XV-04 | RL7-TNK-101-XV-04 |  |  | BREDDO MIXER SEAL FLUSH SOLENOID VALVE | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 6 | 4 | 24 VDC DO | 5069-OB16
245 | RL7-DRM-101-AH-01 | RL7-DRM-101-AH-01 | SND317 |  | BREDO DUMPER ALARM HORN | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 6 | 9 | 24 VDC DO | 5069-OB16
246 | RL7-DRM-101-PL-01R | RL7-DRM-101-PL-01R | LT315 |  | BREDO DUMPER RED PILOT LIGHT | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 6 | 10 | 24 VDC DO | 5069-OB16
247 | RL7-DRM-101-PL-01Y | RL7-DRM-101-PL-01Y | LT316 |  | BREDO DUMPER YELLOW PILOT LIGHT | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 6 | 11 | 24 VDC DO | 5069-OB16
248 | RL7-DRM-101-PL-01G | RL7-DRM-101-PL-01G | LT314 |  | BREDO DUMPER GREEN PILOT LIGHT | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 6 | 12 | 24 VDC DO | 5069-OB16
249 | RL7-DRM-101-PBL-02 | RL7-DRM-101-PBL-02 | PBL114 |  | BREDDO DUMPER LIGHT CURTAIN RESET PB PILOT LIGHT | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 1 | 24 VDC DO | 5069-OB16
250 | RL7-DRM-101-PBL-03 | RL7-DRM-101-PBL-03 | PBL116 |  | BREDDO DUMPER QR SCANNED PB PILOT LIGHT | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 2 | 24 VDC DO | 5069-OB16
251 | RL7-DRM-101-XY-06 | RL7-DRM-101-XY-06 | SOL301 |  | BREDDO DUMPER SEAL SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 3 | 24 VDC DO | 5069-OB16
252 | RL7-DRM-101-XY-07 | RL7-DRM-101-XY-07 | SOL302 |  | BREDDO DUMPER UNSEAL SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 4 | 24 VDC DO | 5069-OB16
253 | RL7-DRM-101-XY-08 | RL7-DRM-101-XY-08 | SOL303 |  | BREDDO DUMPER PIVOT SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 5 | 24 VDC DO | 5069-OB16
254 | RL7-DRM-101-XY-09 | RL7-DRM-101-XY-09 | SOL304 |  | BREDDO DUMPER REVERSE PIVOT SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 6 | 24 VDC DO | 5069-OB16
255 | RL7-DRM-101-XY-10 | RL7-DRM-101-XY-10 | SOL305 |  | BREDDO DUMPER SLOW SPEED SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 7 | 24 VDC DO | 5069-OB16
256 | RL7-DRM-101-XY-01B | RL7-DRM-101-XY-01B | SOL306 |  | BREDDO DUMPER DISCHARGE SLIDE GATE CLOSE SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 8 | 24 VDC DO | 5069-OB16
257 | RL7-DRM-101-XY-01A | RL7-DRM-101-XY-01A | SOL307 |  | BREDDO DUMPER DISCHARGE SLIDE GATE OPEN SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 9 | 24 VDC DO | 5069-OB16
258 | RL7-DRM-101-XY-02B | RL7-DRM-101-XY-02B | SOL308 |  | BREDDO DUMPER MIXER SUPPLY SLIDE GATE CLOSE SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 10 | 24 VDC DO | 5069-OB16
259 | RL7-DRM-101-XY-02A | RL7-DRM-101-XY-02A | SOL309 |  | BREDDO DUMPER MIXER SUPPLY SLIDE GATE OPEN SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 11 | 24 VDC DO | 5069-OB16
260 | RL7-DRM-101-XY-03 | RL7-DRM-101-XY-03 | SOL310 |  | BREDDO DUMPER VIBRATOR SOLENOID | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 7 | 12 | 24 VDC DO | 5069-OB16
261 | RL7-TNK-101-FVI-02 | RL7-TNK-101-FVI-02 |  |  | BREDDO MIXER CIPS CONTROL VALVE POSITION FEEDBACK | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 9 | 0 | 4-20 mA AI | 5069-IF8
262 | RL7-TNK-101-FIT-02 | RL7-TNK-101-FIT-02 |  |  | BREDDO MIXER CIPS FLOW | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 9 | 1 | 4-20 mA AI | 5069-IF8
263 | RL7-TNK-101-FCV-02 | RL7-TNK-101-FCV-02 |  |  | BREDDO MIXER CIPS CONTROL VALVE | DG7010 | PROC | RL7-BRED-RIO1 | 11 | 10 | 0 | 4-20 mA AO | 5069-OF8
264 |  | RL7-LINE-PBL-01 |  |  | ROLL LINE E-STOP PB PILOT LIGHT | DG7010 | PROC | RL7-INTSL-RIO1 | 18 | 3 | 4 | 24 VDC DO | 5069-OB16
265 |  | RL7-LINE-AH-01 |  |  | ROLL LINE 7 ALARM HORN | DG7010 | PROC | RL7-INTSL-RIO1 | 18 | 3 | 5 | 24 VDC DO | 5069-OB16
266 |  | RL7-LINE-PL-01R |  |  | ROLL LINE 7 RED PILOT LIGHT | DG7010 | PROC | RL7-INTSL-RIO1 | 18 | 3 | 6 | 24 VDC DO | 5069-OB16
267 |  | RL7-LINE-PL-01Y |  |  | ROLL LINE 7 YELLOW PILOT LIGHT | DG7010 | PROC | RL7-INTSL-RIO1 | 18 | 3 | 7 | 24 VDC DO | 5069-OB16
268 |  | RL7-LINE-PL-01G |  |  | ROLL LINE 7 GREEN PILOT LIGHT | DG7010 | PROC | RL7-INTSL-RIO1 | 18 | 3 | 8 | 24 VDC DO | 5069-OB16
269 | RL7-TNK-101-FVI-01 | RL7-TNK-101-FVI-01 |  |  | BREDDO MIXER WATER CONTROL VALVE | DG7010 | INTSL | RL7-INTSL-RIO1 | 18 | 8 | 2 | 4-20 mA AI | 5069-IF8
270 | RL7-TNK-101-FIT-01 | RL7-TNK-101-FIT-01 |  |  | BREDDO MIXER WATER SUPPLY FLOW | DG7010 | INTSL | RL7-INTSL-RIO1 | 18 | 9 | 3 | 4-20 mA AI | 5069-IF8 | 0 - 300 GPM
271 | RL7-TNK-101-FCV-01 | RL7-TNK-101-FCV-01 |  |  | BREDDO MIXER WATER CONTROL VALVE | DG7010 | INTSL | RL7-INTSL-RIO1 | 18 | 12 | 3 | 4-20 mA AO | 5069-OF8
272 |  | RL7-DRM-101.M1 |  |  | BREDDO DUMPER ENABLE | DG7010 | MCC | RL7-INTSL-RIO1 | 18 | 14 | 8 | 24 VDC DO | 5069-OB16
273 |  | RL7-LINE-PB-01 |  |  | ROLL LINE E-STOP PB SAFETY INPUT CH1 | DG7010 | PROC | RL7-INTSL-RIO1 | 18 | 15 | 0 | 24 VDC SI | 5069-IB8S
274 |  | RL7-LINE-PB-01 |  |  | ROLL LINE E-STOP PB SAFETY INPUT CH2 | DG7010 | PROC | RL7-INTSL-RIO1 | 18 | 15 | 1 | 24 VDC SI | 5069-IB8S
275 | RL7-AGC-101-PB-01 | RL7-AGC-101-PB-01 | PB706161 | OS11A | FRESH AUGER CART 1 E-STOP SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 1 | 6 | 24 VDC SI | 5069-IB8S
276 | RL7-AGC-101-PB-01 | RL7-AGC-101-PB-01 | PB706161 | OS11A | FRESH AUGER CART 1 E-STOP SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 1 | 7 | 24 VDC SI | 5069-IB8S
277 | RL7-AGC-101-PB-02 | RL7-AGC-101-PB-02 | PB907021 | JIC11B, OS11A | FRESH AUGER CART 1 PUMP FEEDER JOG PB | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 4 | 0 | 24 VDC DI | 5069-IB16
278 | RL7-AGC-101-ZSS-01 | RL7-AGC-101-ZSS-01 | PRS906021 | JIC11B | FRESH AUGER CART 1 SAFETY GRATE SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 1 | 0 | 24 VDC SI | 5069-IB8S
279 | RL7-AGC-101-ZSS-01 | RL7-AGC-101-ZSS-01 | PRS906021 | JIC11B | FRESH AUGER CART 1 SAFETY GRATE SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 1 | 1 | 24 VDC SI | 5069-IB8S
280 | RL7-AGC-101-ZSS-02 | RL7-AGC-101-ZSS-02 | PRS906061 | JIC11B | FRESH AUGER CART 1 CLEANOUT HATCH SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 1 | 2 | 24 VDC SI | 5069-IB8S
281 | RL7-AGC-101-ZSS-02 | RL7-AGC-101-ZSS-02 | PRS906061 | JIC11B | FRESH AUGER CART 1 CLEANOUT HATCH SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 1 | 3 | 24 VDC SI | 5069-IB8S
282 | RL7-AGC-101-ZSS-03 | RL7-AGC-101-ZSS-03 | PRS906101 | JIC11B | FRESH AUGER CART 1 PUMP DISCHARGE SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 1 | 4 | 24 VDC SI | 5069-IB8S
283 | RL7-AGC-101-ZSS-03 | RL7-AGC-101-ZSS-03 | PRS906101 | JIC11B | FRESH AUGER CART 1 PUMP DISCHARGE SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 1 | 5 | 24 VDC SI | 5069-IB8S
284 | RL7-AGC-101-ZSS-04 | RL7-AGC-101-ZSS-04 | PRS906211 | JIC11B | FRESH AUGER CART 1 SANITATION DISCHARGE GUARD SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 3 | 0 | 24 VDC SI | 5069-IB8S
285 | RL7-AGC-101-ZSS-04 | RL7-AGC-101-ZSS-04 | PRS906211 | JIC11B | FRESH AUGER CART 1 SANITATION DISCHARGE GUARD SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 3 | 1 | 24 VDC SI | 5069-IB8S
286 | RL7-AGC-102-PB-01 | RL7-AGC-102-PB-01 | PB906161 | JIC12B, OS12A | FRESH AUGER CART 2 E-STOP SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 1 | 6 | 24 VDC SI | 5069-IB8S
287 | RL7-AGC-102-PB-01 | RL7-AGC-102-PB-01 | PB906161 | JIC12B, OS12A | FRESH AUGER CART 2 E-STOP SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 1 | 7 | 24 VDC SI | 5069-IB8S
288 | RL7-AGC-102-PB-02 | RL7-AGC-102-PB-02 | PB1007021 | JIC12B, OS12A | FRESH AUGER CART 2 PUMP FEEDER JOG PB | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 4 | 0 | 24 VDC DI | 5069-IB16
289 | RL7-AGC-102-PBL-01 | RL7-AGC-102-PBL-01 | PB1006161 | JIC12B, OS12A | FRESH AUGER CART 2 PUMP E-STOP PB PILOT LIGHT | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 6 | 8 | 24 VDC DO | 5069-OB16
290 | RL7-AGC-102-ZSS-01 | RL7-AGC-102-ZSS-01 | PRS1006021 | JIC12B | FRESH AUGER CART 2 SAFETY GRATE SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 1 | 0 | 24 VDC SI | 5069-IB8S
291 | RL7-AGC-102-ZSS-01 | RL7-AGC-102-ZSS-01 | PRS1006021 | JIC12B | FRESH AUGER CART 2 SAFETY GRATE SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 1 | 1 | 24 VDC SI | 5069-IB8S
292 | RL7-AGC-102-ZSS-02 | RL7-AGC-102-ZSS-02 | PRS1006061 | JIC12B | FRESH AUGER CART 2 CLEANOUT HATCH SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 1 | 2 | 24 VDC SI | 5069-IB8S
293 | RL7-AGC-102-ZSS-02 | RL7-AGC-102-ZSS-02 | PRS1006061 | JIC12B | FRESH AUGER CART 2 CLEANOUT HATCH SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 1 | 3 | 24 VDC SI | 5069-IB8S
294 | RL7-AGC-102-ZSS-03 | RL7-AGC-102-ZSS-03 | PRS1006101 | JIC12B | FRESH AUGER CART 2 PUMP DISCHARGE SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 1 | 4 | 24 VDC SI | 5069-IB8S
295 | RL7-AGC-102-ZSS-03 | RL7-AGC-102-ZSS-03 | PRS1006101 | JIC12B | FRESH AUGER CART 2 PUMP DISCHARGE SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 1 | 5 | 24 VDC SI | 5069-IB8S
296 | RL7-AGC-102-ZSS-04 | RL7-AGC-102-ZSS-04 | PRS1006211 | JIC12B | FRESH AUGER CART 2 SANITATION DISCHARGE GUARD SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 3 | 0 | 24 VDC SI | 5069-IB8S
297 | RL7-AGC-102-ZSS-04 | RL7-AGC-102-ZSS-04 | PRS1006211 | JIC12B | FRESH AUGER CART 2 SANITATION DISCHARGE GUARD SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 3 | 1 | 24 VDC SI | 5069-IB8S
298 |  | RL7-MLT-104.M1 |  |  | FRESH AUGER CART 1 DUMPER ENABLE | DG7011 | MCC | RL7-INTSL-RIO1 | 18 | 14 | 2 | 24 VDC DO | 5069-OB16
299 | RL7-MLT-104-HS-01 | RL7-MLT-104-HS-01 | SS705211 | OS9A | FRESH AUGER CART 1 DUMPER PALLET RETENTION SELECTOR SWITCH | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 4 | 5 | 24 VDC DI | 5069-IB16
300 | RL7-MLT-104-HS-02 | RL7-MLT-104-HS-02 | SS705221 | OS9A | FRESH AUGER CART 1 DUMPER BAG RETENTION SELECTOR SWITCH | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 4 | 6 | 24 VDC DI | 5069-IB16
301 | RL7-MLT-104-PB-01 | RL7-MLT-104-PB-01 | PB706161 | OS9A | FRESH AUGER CART 1 DUMPER E-STOP SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 2 | 0 | 24 VDC SI | 5069-IB8S
302 | RL7-MLT-104-PB-01 | RL7-MLT-104-PB-01 | PB706161 | OS9A | FRESH AUGER CART 1 DUMPER E-STOP SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 2 | 1 | 24 VDC SI | 5069-IB8S
303 | RL7-MLT-104-PB-02 | RL7-MLT-104-PB-02 | PB705191 | OS9A | FRESH AUGER CART 1 DUMPER UP PB | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 4 | 7 | 24 VDC DI | 5069-IB16
304 | RL7-MLT-104-PB-03 | RL7-MLT-104-PB-03 | PB705201 | OS9A | FRESH AUGER CART 1 DUMPER DOWN PB | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 4 | 8 | 24 VDC DI | 5069-IB16
305 | RL7-MLT-104-PBL-01 | RL7-MLT-104-PBL-01 | PB706161 | OS9A | FRESH AUGER CART 1 DUMPER E-STOP PB PILOT LIGHT | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 6 | 0 | 24 VDC DO | 5069-OB16
306 | RL7-MLT-104-PSL-01 | RL7-MLT-104-PSL-01 | PRG705171 | OS9A | FRESH AUGER CART 1 DUMPER PRESSURE REGULATOR | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 4 | 3 | 24 VDC DI | 5069-IB16
307 | RL7-MLT-104-XY-101A | RL7-MLT-104-XY-101A | SOL705041 | OS9A | FRESH AUGER CART 1 DUMPER ENGAGE PALLET RETENTION SOLENOID | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 6 | 4 | 24 VDC DO | 5069-OB16
308 | RL7-MLT-104-XY-101B | RL7-MLT-104-XY-101B | SOL705041 | OS9A | FRESH AUGER CART 1 DUMPER RELEASE PALLET RETENTION SOLENOID | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 6 | 5 | 24 VDC DO | 5069-OB16
309 | RL7-MLT-104-XY-102A | RL7-MLT-104-XY-102A | SOL705061 | OS9A | FRESH AUGER CART 1 DUMPER ENGAGE BAG RETENTION SOLENOID | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 6 | 6 | 24 VDC DO | 5069-OB16
310 | RL7-MLT-104-XY-102B | RL7-MLT-104-XY-102B | SOL705061 | OS9A | FRESH AUGER CART 1 DUMPER RELEASE BAG RETENTION SOLENOID | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 6 | 7 | 24 VDC DO | 5069-OB16
311 | RL7-MLT-104-XY-103A | RL7-MLT-104-XY-103A | SOL705031 | OS9A | FRESH AUGER CART 1 DUMPER HYDRAULIC UP SOLENOID | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 6 | 2 | 24 VDC DO | 5069-OB16
312 | RL7-MLT-104-XY-103B | RL7-MLT-104-XY-103B | SOL705031 | OS9A | FRESH AUGER CART 1 DUMPER HYDRAULIC DOWN SOLENOID | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 6 | 3 | 24 VDC DO | 5069-OB16
313 | RL7-MLT-104-ZSC-01 | RL7-MLT-104-ZSC-01 | PRS705151 | OS9A | FRESH AUGER CART 1 DUMPER IN DOWN POSITION | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 4 | 1 | 24 VDC DI | 5069-IB16
314 | RL7-MLT-104-ZSS-01 | RL7-MLT-104-ZSS-01 | PRS706061 | OS9A | FRESH AUGER CART 1 DUMPER SAFETY LOCK PIN 1 SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 2 | 4 | 24 VDC SI | 5069-IB8S
315 | RL7-MLT-104-ZSS-01 | RL7-MLT-104-ZSS-01 | PRS706061 | OS9A | FRESH AUGER CART 1 DUMPER SAFETY LOCK PIN 1 SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 2 | 5 | 24 VDC SI | 5069-IB8S
316 | RL7-MLT-104-ZSS-02 | RL7-MLT-104-ZSS-02 | PRS706101 | OS9A | FRESH AUGER CART 1 DUMPER SAFETY LOCK PIN 2 SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 2 | 6 | 24 VDC SI | 5069-IB8S
317 | RL7-MLT-104-ZSS-02 | RL7-MLT-104-ZSS-02 | PRS706101 | OS9A | FRESH AUGER CART 1 DUMPER SAFETY LOCK PIN 2 SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 2 | 7 | 24 VDC SI | 5069-IB8S
318 | RL7-MLT-104-ZSS-03 | RL7-MLT-104-ZSS-03 | PRS706021 | OS9A | FRESH AUGER CART 1 DUMPER SAFETY GATE SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 2 | 2 | 24 VDC SI | 5069-IB8S
319 | RL7-MLT-104-ZSS-03 | RL7-MLT-104-ZSS-03 | PRS706021 | OS9A | FRESH AUGER CART 1 DUMPER SAFETY GATE SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC1-RIO1 | 8 | 2 | 3 | 24 VDC SI | 5069-IB8S
320 |  | RL7-MLT-105.M1 |  |  | FRESH AUGER CART 2 DUMPER ENABLE | DG7011 | MCC | RL7-INTSL-RIO1 | 18 | 14 | 3 | 24 VDC DO | 5069-OB16
321 | RL7-MLT-105-HS-01 | RL7-MLT-105-HS-01 | SS805211 | OS10A | FRESH AUGER CART 2 DUMPER PALLET RETENTION SELECTOR SWITCH | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 4 | 5 | 24 VDC DI | 5069-IB16
322 | RL7-MLT-105-HS-02 | RL7-MLT-105-HS-02 | SS805221 | OS10A | FRESH AUGER CART 2 DUMPER BAG RETENTION SELECTOR SWITCH | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 4 | 6 | 24 VDC DI | 5069-IB16
323 | RL7-MLT-105-PB-01 | RL7-MLT-105-PB-01 | PB806161 | OS10A | FRESH AUGER CART 2 DUMPER E-STOP SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 2 | 0 | 24 VDC SI | 5069-IB8S
324 | RL7-MLT-105-PB-01 | RL7-MLT-105-PB-01 | PB806161 | OS10A | FRESH AUGER CART 2 DUMPER E-STOP SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 2 | 1 | 24 VDC SI | 5069-IB8S
325 | RL7-MLT-105-PB-02 | RL7-MLT-105-PB-02 | PB805151 | OS10A | FRESH AUGER CART 2 DUMPER UP PB | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 4 | 7 | 24 VDC DI | 5069-IB16
326 | RL7-MLT-105-PB-03 | RL7-MLT-105-PB-03 | PB805161 | OS10A | FRESH AUGER CART 2 DUMPER DOWN PB | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 4 | 8 | 24 VDC DI | 5069-IB16
327 | RL7-MLT-105-PBL-01 | RL7-MLT-105-PBL-01 | PB806161 | OS10A | FRESH AUGER CART 2 DUMPER E-STOP PB PILOT LIGHT | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 6 | 0 | 24 VDC DO | 5069-OB16
328 | RL7-MLT-105-PSL-01 | RL7-MLT-105-PSL-01 | PRG805171 | OS10A | FRESH AUGER CART 2 REGULATOR LOW PRESSURE SWITCH | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 4 | 3 | 24 VDC DI | 5069-IB16
329 | RL7-MLT-105-XY-101A | RL7-MLT-105-XY-101A | SOL805041 | OS10A | FRESH AUGER CART 2 DUMPER ENGAGE PALLET RETENTION SOLENOID | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 6 | 4 | 24 VDC DO | 5069-OB16
330 | RL7-MLT-105-XY-101B | RL7-MLT-105-XY-101B | SOL805041 | OS10A | FRESH AUGER CART 2 DUMPER RELEASE PALLET RETENTION SOLENOID | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 6 | 5 | 24 VDC DO | 5069-OB16
331 | RL7-MLT-105-XY-102A | RL7-MLT-105-XY-102A | SOL805061 | OS10A | FRESH AUGER CART 2 DUMPER ENGAGE BAG RETENTION SOLENOID | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 6 | 6 | 24 VDC DO | 5069-OB16
332 | RL7-MLT-105-XY-102B | RL7-MLT-105-XY-102B | SOL805061 | OS10A | FRESH AUGER CART 2 DUMPER RELEASE BAG RETENTION SOLENOID | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 6 | 7 | 24 VDC DO | 5069-OB16
333 | RL7-MLT-105-XY-103A | RL7-MLT-105-XY-103A | SOL805021 | OS10A | FRESH AUGER CART 2 DUMPER HYDRAULIC UP SOLENOID | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 6 | 2 | 24 VDC DO | 5069-OB16
334 | RL7-MLT-105-XY-103B | RL7-MLT-105-XY-103B | SOL805021 | OS10A | FRESH AUGER CART 2 DUMPER HYDRAULIC DOWN SOLENOID | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 6 | 3 | 24 VDC DO | 5069-OB16
335 | RL7-MLT-105-ZSC-01 | RL7-MLT-105-ZSC-01 | PRS805151 | OS10A | FRESH AUGER CART 2 DUMPER IN DOWN POSITION | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 4 | 1 | 24 VDC DI | 5069-IB16
336 | RL7-MLT-105-ZSS-01 | RL7-MLT-105-ZSS-01 | PRS806061 | OS10A | FRESH AUGER CART 2 DUMPER SAFETY LOCK PIN 1 SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 2 | 4 | 24 VDC SI | 5069-IB8S
337 | RL7-MLT-105-ZSS-01 | RL7-MLT-105-ZSS-01 | PRS806061 | OS10A | FRESH AUGER CART 2 DUMPER SAFETY LOCK PIN 1 SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 2 | 5 | 24 VDC SI | 5069-IB8S
338 | RL7-MLT-105-ZSS-02 | RL7-MLT-105-ZSS-02 | PRS806101 | OS10A | FRESH AUGER CART 2 DUMPER SAFETY LOCK PIN 2 SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 2 | 6 | 24 VDC SI | 5069-IB8S
339 | RL7-MLT-105-ZSS-02 | RL7-MLT-105-ZSS-02 | PRS806101 | OS10A | FRESH AUGER CART 2 DUMPER SAFETY LOCK PIN 2 SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 2 | 7 | 24 VDC SI | 5069-IB8S
340 | RL7-MLT-105-ZSS-03 | RL7-MLT-105-ZSS-03 | PRS806021 | OS10A | FRESH AUGER CART 2 DUMPER SAFETY GATE SAFETY INPUT CH1 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 2 | 2 | 24 VDC SI | 5069-IB8S
341 | RL7-MLT-105-ZSS-03 | RL7-MLT-105-ZSS-03 | PRS806021 | OS10A | FRESH AUGER CART 2 DUMPER SAFETY GATE SAFETY INPUT CH2 | DG7011 | PROC | RL7-FAGC2-RIO1 | 9 | 2 | 3 | 24 VDC SI | 5069-IB8S
342 | RL7-CNV-115-PBL-01 | RL7-CNV-108-PBL-01 |  |  | INCLINE BELT CONVEYOR E-STOP PUSHBUTTON PILOT LIGHT | DG7012 | PROC | RL7-IPA2-RIO1 | 7 | 7 | 1 | 24 VDC DO | 5069-OB16
343 | RL7-GRR-101-PBL-01 | RL7-GRR-102-PBL-01 |  |  | GRINDER PLATFORM E-STOP PUSHBUTTON PILOT LIGHT | DG7012 | PROC | RL7-IPA2-RIO1 | 7 | 7 | 0 | 24 VDC DO | 5069-OB16
344 |  | RL7-MLT-106.M1 |  |  | PRE-MIXER COLUMN DUMPER | DG7012 | MCC | RL7-INTSL-RIO1 | 18 | 14 | 9 | 24 VDC DO | 5069-OB16
345 | RL7-PRM-101-ZSC-03 | RL7-MLT-106-PB-01 | PB2506011 | JIC3B | PRE-MIXER COLUMN DUMPER RAISE PB | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 1 | 24 VDC DI | 5069-IB16
346 | RL7-PRM-101-ZSC-04 | RL7-MLT-106-PB-02 | PB2506021 | JIC3B | PRE-MIXER COLUMN DUMPER LOWER PB | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 2 | 24 VDC DI | 5069-IB16
347 | RL7-MLT-106-PB-01 | RL7-MLT-106-PB-03 | PB2506031 | JIC3B | PRE-MIXER COLUMN DUMPER STOP PB | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 3 | 24 VDC DI | 5069-IB16
348 | RL7-MLT-106-PB-04 | RL7-MLT-106-PB-04 | PB2505011 | JIC3B | PRE-MIXER COLUMN DUMPER E-STOP PUSHBUTTON SAFETY INPUT CH1 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 4 | 2 | 24 VDC SI | 5069-IB8S
349 | RL7-MLT-106-PB-04 | RL7-MLT-106-PB-04 | PB2505011 | JIC3B | PRE-MIXER COLUMN DUMPER E-STOP PUSHBUTTON SAFETY INPUT CH2 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 4 | 3 | 24 VDC SI | 5069-IB8S
350 |  | RL7-MLT-106-PB-05 | PB505161 | OS7C | PRE-MIXER COLUMN DUMPER ENTRY REQUEST PB | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 5 | 0 | 24 VDC SI | 5069-IB8S
351 |  | RL7-MLT-106-PB-06 | PB505191 | OS7C | PRE-MIXER COLUMN DUMPER RESET GATE LOCK PB | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 5 | 1 | 24 VDC SI | 5069-IB8S
352 | RL7-MLT-106-PBL-01 | RL7-MLT-106-PBL-04 | PB2505011 | JIC3B | PRE-MIXER COLUMN DUMPER E-STOP PB PILOT LIGHT | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 7 | 24 VDC DO | 5069-OB16
353 | RL7-MLT-106-ZSC-03 | RL7-MLT-106-ZSC-01 | PRS2506111 | JIC3B | PRE-MIXER COLUMN DUMPER LOWER LIMIT STOP | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 6 | 24 VDC DI | 5069-IB16
354 | RL7-MLT-106-PB-03 | RL7-MLT-106-ZSC-02 | PRS2506091 | JIC3B | PRE-MIXER COLUMN DUMPER UPPER LIMIT STOP | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 5 | 24 VDC DI | 5069-IB16
355 | RL7-MLT-106-PB-02 | RL7-MLT-106-ZSC-03 | PRS2506071 | JIC3B | PRE-MIXER COLUMN DUMPER OVER TRAVEL LIMIT | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 4 | 24 VDC DI | 5069-IB16
356 |  | RL7-MLT-106-ZSS-04 | PRS306021 | OS9A/JIC9B | PRE-MIXER COLUMN DUMPER IN DOWN POSITION SAFETY INPUT 1 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 5 | 2 | 24 VDC SI | 5069-IB8S
357 |  | RL7-MLT-106-ZSS-04 | PRS306021 | OS9A/JIC9B | PRE-MIXER COLUMN DUMPER IN DOWN POSITION SAFETY INPUT 2 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 5 | 3 | 24 VDC SI | 5069-IB8S
358 |  | RL7-MLT-106-ZSS-05 | PRS306021 | OS9A/JIC9B | PRE-MIXER COLUMN DUMPER SAFETY GATE ACTIVE SAFETY INPUT 1 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 5 | 4 | 24 VDC SI | 5069-IB8S
359 |  | RL7-MLT-106-ZSS-05 | PRS306021 | OS9A/JIC9B | PRE-MIXER COLUMN DUMPER SAFETY GATE ACTIVE SAFETY INPUT 2 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 5 | 5 | 24 VDC SI | 5069-IB8S
360 |  | RL7-PRM-101-FCV-01 |  |  | PRE-MIXER CIPS FLOW CONTROL VALVE | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 11 | 0 | 4-20 mA AO | 5069-OF8
361 | RL7-AGC-201-TIT-01 | RL7-PRM-101-FIT-01 |  |  | PRE-MIXER CIPS FLOW | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 10 | 0 | 4-20 mA AI | 5069-IF8
362 | RL7-AGC-201-TIT-02 | RL7-PRM-101-FVI-01 |  |  | PRE-MIXER CIPS CONTROL VALVE POSITION FEEDBACK | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 10 | 1 | 4-20 mA AI | 5069-IF8
363 | RL7-PRM-101-PB-01 | RL7-PRM-101-PB-01 |  |  | PRE-MIXER E-STOP PB SAFETY INPUT CH1 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 4 | 0 | 24 VDC SI | 5069-IB8S
364 | RL7-PRM-101-PB-01 | RL7-PRM-101-PB-01 |  |  | PRE-MIXER E-STOP PB SAFETY INPUT CH2 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 4 | 1 | 24 VDC SI | 5069-IB8S
365 | RL7-PRM-101-PBL-01 | RL7-PRM-101-PBL-01 |  |  | PRE-MIXER E-STOP PB PILOT LIGHT | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 6 | 24 VDC DO | 5069-OB16
366 | RL7-PRM-101-PSL-01 | RL7-PRM-101-PSL-01 | PRG107011 | JIC2B | PRE-MIXER PRESSURE REGULATOR | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 0 | 24 VDC DI | 5069-IB16
367 |  | RL7-PRM-101-XV-05 |  |  | PRE-MIXER CIPS MIX PROOF VALVE OPEN SOLENOID | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 14 | 24 VDC DO | 5069-OB16
368 | RL7-PRM-101-XV-05 | RL7-PRM-101-XV-05 |  |  | PRE-MIXER SANITATION VALVE OPEN SOLENOID | DG7012 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 11 | 24 VDC DO | 5069-OB16
369 |  | RL7-PRM-101-XV-06 |  |  | PRE-MIXER RAW PRODUCT COOKER 1 FILL VALVE OPEN SOLENOID | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 8 | 24 VDC DO | 5069-OB16
370 |  | RL7-PRM-101-XV-07 |  |  | PRE-MIXER RAW PRODUCT COOKER 2 FILL VALVE OPEN SOLENOID | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 9 | 24 VDC DO | 5069-OB16
371 |  | RL7-PRM-101-XV-08 |  |  | PRE-MIXER GUM / CIP SUPPLY MIX PROOF VALVE OPEN SOLENOID | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 10 | 24 VDC DO | 5069-OB16
372 |  | RL7-PRM-101-XV-09 |  |  | PRE-MIXER CIP RETURN MIX PROOF VALVE OPEN SOLENOID | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 11 | 24 VDC DO | 5069-OB16
373 | RL7-PRM-101-XY-01A | RL7-PRM-101-XY-01A | SOL107041 | JIC2B | PRE-MIXER MIXER COVER OPEN SOLENOID | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 2 | 24 VDC DO | 5069-OB16
374 | RL7-PRM-101-XY-01B | RL7-PRM-101-XY-01B | SOL107041 | JIC2B | PRE-MIXER MIXER COVER CLOSE SOLENOID | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 3 | 24 VDC DO | 5069-OB16
375 | RL7-PRM-101-XY-02A | RL7-PRM-101-XY-02A | SOL107061 | JIC2B | PRE-MIXER SAFETY GRATE ENGAGE SOLENOID | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 4 | 24 VDC DO | 5069-OB16
376 | RL7-PRM-101-XY-02B | RL7-PRM-101-XY-02B | SOL107061 | JIC2B | PRE-MIXER SAFETY GRATE RELEASE SOLENOID | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 9 | 5 | 24 VDC DO | 5069-OB16
377 | RL7-PRM-101-XYS-01A | RL7-PRM-101-XYS-04A | SOL106171 | JIC2B | PRE-MIXER SAFETY AIR DUMP SOLENOID A | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 6 | 0 | 24 VDC SO | 5069-OBV8S
378 | RL7-PRM-101-XYS-01B | RL7-PRM-101-XYS-04B | SOL106171 | JIC2B | PRE-MIXER SAFETY AIR DUMP SOLENOID B | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 6 | 1 | 24 VDC SO | 5069-OBV8S
379 | RL7-PRM-101-ZSC-01 | RL7-PRM-101-ZSC-01 | PRS107171 | JIC2B | PRE-MIXER LOCKBAR ENGAGED | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 8 | 7 | 24 VDC DI | 5069-IB16
380 | RL7-PRM-101-ZSC-02 | RL7-PRM-101-ZSC-02 | VLV107221 | JIC2B | PRE-MIXER SAFETY GRATE LOCKED | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 8 | 10 | 24 VDC DI | 5069-IB16
381 | RL7-PRM-101-ZSC-01A | RL7-PRM-101-ZSC-04A | SOL106171 | JIC2B | PRE-MIXER AIR DUMP SOLENOID A LIMIT SWITCH SAFETY INPUT CH1 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 3 | 4 | 24 VDC SI | 5069-IB8S
382 | RL7-PRM-101-ZSC-01B | RL7-PRM-101-ZSC-04B | SOL106171 | JIC2B | PRE-MIXER AIR DUMP SOLENOID B LIMIT SWITCH SAFETY INPUT CH2 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 3 | 5 | 24 VDC SI | 5069-IB8S
383 |  | RL7-PRM-101-ZSC-05 |  |  | PRE-MIXER CIPS MIX PROOF VALVE CLOSED LIMIT SWITCH | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 8 | 12 | 24 VDC DI | 5069-IB16
384 | RL7-PRM-101-ZSC-05 | RL7-PRM-101-ZSC-05 |  |  | PRE-MIXER SANITATION VALVE CLOSED LIMIT SWITCH | DG7012 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 13 | 24 VDC DI | 5069-IB16
385 |  | RL7-PRM-101-ZSC-06 |  |  | PRE-MIXER RAW PRODUCT COOKER 1 FILL VALVE CLOSED LIMIT SWITCH | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 9 | 24 VDC DI | 5069-IB16
386 |  | RL7-PRM-101-ZSC-07 |  |  | PRE-MIXER RAW PRODUCT COOKER 2 FILL VALVE CLOSED LIMIT SWITCH | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 11 | 24 VDC DI | 5069-IB16
387 |  | RL7-PRM-101-ZSC-08 |  |  | PRE-MIXER GUM / CIP SUPPLY MIX PROOF VALVE CLOSED LIMIT SWITCH | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 13 | 24 VDC DI | 5069-IB16
388 |  | RL7-PRM-101-ZSC-09 |  |  | PRE-MIXER CIP RETURN MIX PROOF VALVE CLOSED LIMIT SWITCH | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 15 | 24 VDC DI | 5069-IB16
389 | RL7-PRM-101-ZSO-01 | RL7-PRM-101-ZSO-01 | PRS107191 | JIC2B | PRE-MIXER LOCKBAR RELEASED | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 8 | 8 | 24 VDC DI | 5069-IB16
390 | RL7-PRM-101-ZSO-02 | RL7-PRM-101-ZSO-02 | VLV107221 | JIC2B | PRE-MIXER SAFETY GRATE RELEASED | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 8 | 9 | 24 VDC DI | 5069-IB16
391 | RL7-PRM-101-ZSS-01 | RL7-PRM-101-ZSO-03 | PRS107151 | JIC2B | PRE-MIXER COVER OPEN | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 8 | 6 | 24 VDC DI | 5069-IB16
392 |  | RL7-PRM-101-ZSO-05 |  |  | PRE-MIXER CIPS MIX PROOF VALVE OPEN LIMIT SWITCH | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 8 | 11 | 24 VDC DI | 5069-IB16
393 | RL7-PRM-101-ZSO-05 | RL7-PRM-101-ZSO-05 |  |  | PRE-MIXER SANITATION VALVE OPEN LIMIT SWITCH | DG7012 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 12 | 24 VDC DI | 5069-IB16
394 | RL7-MLT-106-ZSC-01 | RL7-PRM-101-ZSO-06 |  |  | PRE-MIXER RAW PRODUCT COOKER 1 FILL VALVE OPEN LIMIT SWITCH | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 8 | 24 VDC DI | 5069-IB16
395 |  | RL7-PRM-101-ZSO-07 |  |  | PRE-MIXER RAW PRODUCT COOKER 2 FILL VALVE OPEN LIMIT SWITCH | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 10 | 24 VDC DI | 5069-IB16
396 |  | RL7-PRM-101-ZSO-08 |  |  | PRE-MIXER GUM / CIP SUPPLY MIX PROOF VALVE OPEN LIMIT SWITCH | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 12 | 24 VDC DI | 5069-IB16
397 |  | RL7-PRM-101-ZSO-09 |  |  | PRE-MIXER CIP RETURN MIX PROOF VALVE OPEN LIMIT SWITCH | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 7 | 14 | 24 VDC DI | 5069-IB16
398 | RL7-PRM-101-ZSS-01 | RL7-PRM-101-ZSS-01 | PRS106021 | JIC2B | PRE-MIXER MIXER COVER CLOSED SAFETY INPUT CH1 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 4 | 4 | 24 VDC SI | 5069-IB8S
399 | RL7-PRM-101-ZSS-01 | RL7-PRM-101-ZSS-01 | PRS106021 | JIC2B | PRE-MIXER MIXER COVER CLOSED SAFETY INPUT CH2 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 4 | 5 | 24 VDC SI | 5069-IB8S
400 | RL7-PRM-101-ZSS-02 | RL7-PRM-101-ZSS-02 | PRS106061 | JIC2B | PRE-MIXER SAFETY GRATE SAFETY INPUT CH1 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 3 | 0 | 24 VDC SI | 5069-IB8S
401 | RL7-PRM-101-ZSS-02 | RL7-PRM-101-ZSS-02 | PRS106061 | JIC2B | PRE-MIXER SAFETY GRATE SAFETY INPUT CH2 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 3 | 1 | 24 VDC SI | 5069-IB8S
402 | RL7-PRM-101-ZSS-03 | RL7-PRM-101-ZSS-03 | PRS106091 | JIC2B | PRE-MIXER DISCHARGE SCREW GUARD SAFETY INPUT CH1 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 3 | 2 | 24 VDC SI | 5069-IB8S
403 | RL7-PRM-101-ZSS-03 | RL7-PRM-101-ZSS-03 | PRS106091 | JIC2B | PRE-MIXER DISCHARGE SCREW GUARD SAFETY INPUT CH2 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 3 | 3 | 24 VDC SI | 5069-IB8S
404 | RL7-PRM-101-ZSS-04 | RL7-PRM-101-ZSS-04 | PRS106221 | JIC2B | PRE-MIXER HATCH COVER CLOSED SAFETY INPUT CH1 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 3 | 6 | 24 VDC SI | 5069-IB8S
405 | RL7-PRM-101-ZSS-04 | RL7-PRM-101-ZSS-04 | PRS106221 | JIC2B | PRE-MIXER HATCH COVER CLOSED SAFETY INPUT CH2 | DG7012 | PROC | RL7-PRM-RIO1 | 10 | 3 | 7 | 24 VDC SI | 5069-IB8S
406 |  | RL7-MLT-106-PBL-04 | PB505161 | OS7C | PRE-MIXER COLUMN DUMPER ENTRY REQUEST PB PILOT LIGHT | DG7013 | PROC | RL7-PRM-RIO1 | 10 | 9 | 12 | 24 VDC DO | 5069-OB16
407 |  | RL7-MLT-106-PBL-05 | PB505191 | OS7C | PRE-MIXER COLUMN DUMPER RESET GATE LOCK PB PILOT LIGHT | DG7014 | PROC | RL7-PRM-RIO1 | 10 | 9 | 13 | 24 VDC DO | 5069-OB16
408 | RL7-CKR-101-FCV-02 | RL7-CKR-101-FCV-02 |  |  | COOKER 1 CONTROL VALVE | DG7020 | INTSL | RL7-INTSL-RIO1 | 18 | 12 | 2 | 4-20 mA AO | 5069-OF8
409 | RL7-CKR-101-FIT-02 | RL7-CKR-101-FIT-02 |  |  | COOKER 1 CIPS FLOW | DG7020 | INTSL | RL7-INTSL-RIO1 | 18 | 9 | 2 | 4-20 mA AI | 5069-IF8 | 0 - 300 GPM
410 | RL7-CKR-101-FVI-02 | RL7-CKR-101-FVI-02 |  |  | COOKER 1 CIPS CONTROL VALVE POSITION FEEDBACK | DG7020 | INTSL | RL7-INTSL-RIO1 | 18 | 6 | 4 | 4-20 mA AI | 5069-IF8 | 0 - 10 BAR | [10 empty] | RL7-HTX-101C-TT-02
411 | RL7-CKR-101-PB-01 | RL7-CKR-101-PB-01 |  |  | COOKER 1 E-STOP PB SAFETY INPUT CH1 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 2 | 2 | 24 VDC SI | 5069-IB8S
412 | RL7-CKR-101-PB-01 | RL7-CKR-101-PB-01 |  |  | COOKER 1 E-STOP PB SAFETY INPUT CH2 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 2 | 3 | 24 VDC SI | 5069-IB8S
413 |  | RL7-CKR-101-PB-02 | PB505161 | OS7C | COOKER 1 COLUMN DUMPER ENTRY REQUEST PB | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 3 | 0 | 24 VDC SI | 5069-IB8S
414 |  | RL7-CKR-101-PB-03 | PB505191 | OS7C | COOKER 1 COLUMN DUMPER RESET GATE LOCK PB | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 3 | 1 | 24 VDC SI | 5069-IB8S
415 | RL7-CKR-101-PBL-01 | RL7-CKR-101-PBL-01 |  |  | COOKER 1 E-STOP PB PILOT LIGHT | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 8 | 4 | 24 VDC DO | 5069-OB16
416 |  | RL7-CKR-101-PBL-02 | PB505161 | OS7C | COOKER 1 COLUMN DUMPER ENTRY REQUEST PB PILOT LIGHT | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 5 | 7 | 24 VDC DI | 5069-IB16
417 |  | RL7-CKR-101-PBL-03 | PB505191 | OS7C | COOKER 1 COLUMN DUMPER RESET GATE LOCK PB PILOT LIGHT | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 5 | 8 | 24 VDC DI | 5069-IB16
418 | RL7-CKR-101-PL-01G | RL7-CKR-101-PL-01G |  |  | COOKER 1 GREEN PILOT LIGHT | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 8 | 7 | 24 VDC DO | 5069-OB16
419 | RL7-CKR-101-PL-01R | RL7-CKR-101-PL-01R |  |  | COOKER 1 RED PILOT LIGHT | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 8 | 5 | 24 VDC DO | 5069-OB16
420 | RL7-CKR-101-PL-01Y | RL7-CKR-101-PL-01Y |  |  | COOKER 1 YELLOW PILOT LIGHT | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 8 | 6 | 24 VDC DO | 5069-OB16
421 | RL7-CKR-101-PSL-01 | RL7-CKR-101-PSL-01 | PRG307011 | JIC5B | COOKER 1 REGULATOR LOW PRESSURE SWITCH | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 5 | 2 | 24 VDC DI | 5069-IB16
422 | RL7-CKR-101-TIT-01 | RL7-CKR-101-TIT-01 |  |  | COOKER 1 MIXER SIDE TEMPERATURE TRANSMITTER | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 10 | 0 | 4-20 mA AI | 5069-IF8
423 | RL7-CKR-101-TIT-02 | RL7-CKR-101-TIT-02 |  |  | COOKER 1 MIXER SIDE TEMPERATURE TRANSMITTER | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 10 | 1 | 4-20 mA AI | 5069-IF8
424 | RL7-CKR-101-XY-18A | RL7-CKR-101-XV-18A | SOL307071 | JIC5B | COOKER 1 LEFT DISHCHARGE VALVE OPEN SOLENOID | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 4 | 24 VDC DO | 5069-OB16
425 | RL7-CKR-101-XY-18B | RL7-CKR-101-XV-18B | SOL307071 | JIC5B | COOKER 1 LEFT DISHCHARGE VALVE CLOSE SOLENOID | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 5 | 24 VDC DO | 5069-OB16
426 | RL7-CKR-101-XY-19A | RL7-CKR-101-XV-19A | SOL307161 | JIC5B | COOKER 1 RIGHT DISCHARGE VALVE OPEN SOLENOID | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 6 | 24 VDC DO | 5069-OB16
427 | RL7-CKR-101-XY-19B | RL7-CKR-101-XV-19B | SOL307161 | JIC5B | COOKER 1 RIGHT DISCHARGE VALVE CLOSE SOLENOID | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 7 | 24 VDC DO | 5069-OB16
428 | RL7-CKR-101-XV-25 | RL7-CKR-101-XV-25 |  |  | COOKER 1 CIPS MIX PROOF VALVE OPEN SOLENOID | DG7020 | INTSL | RL7-INTSL-RIO1 | 18 | 3 | 2 | 24 VDC DO | 5069-OB16
429 | RL7-CKR-101-XY-20A | RL7-CKR-101-XY-20A | SOL307061 | JIC5B | COOKER 1 SAFETY GRATE ENGAGE SOLENOID | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 2 | 24 VDC DO | 5069-OB16
430 | RL7-CKR-101-XY-20B | RL7-CKR-101-XY-20B | SOL307061 | JIC5B | COOKER 1 SAFETY GRATE RELEASE SOLENOID | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 3 | 24 VDC DO | 5069-OB16
431 | RL7-CKR-101-XY-22A | RL7-CKR-101-XY-22A | SOL307041 | JIC5B | COOKER 1 COVER OPEN SOLENOID | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 0 | 24 VDC DO | 5069-OB16
432 | RL7-CKR-101-XY-22B | RL7-CKR-101-XY-22B | SOL307041 | JIC5B | COOKER 1 COVER CLOSE SOLENOID | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 1 | 24 VDC DO | 5069-OB16
433 |  | RL7-CKR-101-XY-24 |  |  | COOKER 1 AIR PURGE SOLENOID VALVE | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 15 | 24 VDC DO | 5069-OB16
434 | RL7-CKR-101-XYS-23A | RL7-CKR-101-XYS-23A | SOL306171 | JIC5B | COOKER 1 SAFETY AIR DUMP SOLENOID A | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 4 | 0 | 24 VDC SO | 5069-OBV8S
435 | RL7-CKR-101-XYS-23B | RL7-CKR-101-XYS-23B | SOL306171 | JIC5B | COOKER 1 SAFETY AIR DUMP SOLENOID B | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 4 | 1 | 24 VDC SO | 5069-OBV8S
436 | RL7-CKR-101-ZSC-18 | RL7-CKR-101-ZSC-18 | SOL307111 |  | COOKER 1 LEFT DISCHARGE VALVE CLOSED | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 6 | 7 | 24 VDC DI | 5069-IB16
437 | RL7-CKR-101-ZSC-19 | RL7-CKR-101-ZSC-19 | SOL307131 |  | COOKER 1 RIGHT DISCHARGE VALVE CLOSED | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 6 | 9 | 24 VDC DI | 5069-IB16
438 | RL7-CKR-101-ZSC-20 | RL7-CKR-101-ZSC-20 | VLV307261 |  | COOKER 1 SAFETY GRATE ENGAGED | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 6 | 1 | 24 VDC DI | 5069-IB16
439 | RL7-CKR-101-ZSC-21 | RL7-CKR-101-ZSC-21 | PRS307211 |  | COOKER 1 LOCKBAR ENGAGED | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 5 | 0 | 24 VDC DI | 5069-IB16
440 | RL7-CKR-101-ZSS-23A | RL7-CKR-101-ZSC-23A | SOL306171 | JIC5B | COOKER 1 SAFETY AIR DUMP SOLENOID A STATUS | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 2 | 6 | 24 VDC SI | 5069-IB8S
441 | RL7-CKR-101-ZSS-23A | RL7-CKR-101-ZSC-23B | SOL306171 | JIC5B | COOKER 1 SAFETY AIR DUMP SOLENOID B STATUS | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 2 | 7 | 24 VDC SI | 5069-IB8S
442 | RL7-CKR-101-ZSC-25 | RL7-CKR-101-ZSC-25 |  |  | COOKER 1 CIPS MIX PROOF VALVE CLOSED LIMIT SWITCH | DG7020 | INTSL | RL7-INTSL-RIO1 | 18 | 1 | 1 | 24 VDC DI | 5069-IB16
443 | RL7-CKR-101-ZSO-18 | RL7-CKR-101-ZSO-18 | SOL307111 |  | COOKER 1 LEFT DISCHARGE VALVE OPEN | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 6 | 6 | 24 VDC DI | 5069-IB16
444 | RL7-CKR-101-ZSO-19 | RL7-CKR-101-ZSO-19 | SOL307131 |  | COOKER 1 RIGHT DISCHARGE VALVE OPEN | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 6 | 8 | 24 VDC DI | 5069-IB16
445 | RL7-CKR-101-ZSO-20 | RL7-CKR-101-ZSO-20 | VLV307261 |  | COOKER 1 SAFETY GRATE RELEASED | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 6 | 0 | 24 VDC DI | 5069-IB16
446 | RL7-CKR-101-ZSO-21 | RL7-CKR-101-ZSO-21 | PRS307231 |  | COOKER 1 LOCKBAR RELEASED | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 5 | 1 | 24 VDC DI | 5069-IB16
447 | RL7-CKR-101-ZSO-22 | RL7-CKR-101-ZSO-22 | PRS307191 |  | COOKER 1 COVER OPEN | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 5 | 6 | 24 VDC DI | 5069-IB16
448 | RL7-CKR-101-ZSO-25 | RL7-CKR-101-ZSO-25 |  |  | COOKER 1 CIPS MIX PROOF VALVE OPEN LIMIT SWITCH | DG7020 | INTSL | RL7-INTSL-RIO1 | 18 | 1 | 0 | 24 VDC DI | 5069-IB16
449 | RL7-CKR-101-ZSS-01 | RL7-CKR-101-ZSS-01 | PRS306061 |  | COOKER 1 SAFETY GRATE RFID POSITION SWITCH CH1 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 2 | 4 | 24 VDC SI | 5069-IB8S
450 | RL7-CKR-101-ZSS-01 | RL7-CKR-101-ZSS-01 | PRS306061 |  | COOKER 1 SAFETY GRATE RFID POSITION SWITCH CH2 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 2 | 5 | 24 VDC SI | 5069-IB8S
451 | RL7-CKR-101-ZSS-02 | RL7-CKR-101-ZSS-02 | PRS306021 |  | COOKER 1 COVER CLOSED RFID POSITION SWITCH CH1 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 2 | 0 | 24 VDC SI | 5069-IB8S
452 | RL7-CKR-101-ZSS-02 | RL7-CKR-101-ZSS-02 | PRS306021 |  | COOKER 1 COVER CLOSED RFID POSITION SWITCH CH2 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 2 | 1 | 24 VDC SI | 5069-IB8S
453 | RL7-CKR-101-ZSS-03 | RL7-CKR-101-ZSS-03 | PRS306091 |  | COOKER 1 MIXER HATCH CLOSED RFID POSITION SWITCH CH1 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 1 | 4 | 24 VDC SI | 5069-IB8S
454 | RL7-CKR-101-ZSS-03 | RL7-CKR-101-ZSS-03 | PRS306091 |  | COOKER 1 MIXER HATCH CLOSED RFID POSITION SWITCH CH2 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 1 | 5 | 24 VDC SI | 5069-IB8S
455 |  | RL7-CKR-101-ZSS-04 | PRS306021 | JIC9B,OS9A | COOKER 1 COLUMN DUMPER IN DOWN POSITION SAFETY INPUT CH1 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 3 | 2 | 24 VDC SI | 5069-IB8S
456 |  | RL7-CKR-101-ZSS-04 | PRS306021 | JIC9B,OS9A | COOKER 1 COLUMN DUMPER IN DOWN POSITION SAFETY INPUT CH2 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 3 | 3 | 24 VDC SI | 5069-IB8S
457 |  | RL7-CKR-101-ZSS-05 | PRS306021 | JIC9B,OS9A | COOKER 1 COLUMN DUMPER SAFETY GATE ACTIVE SAFETY INPUT CH1 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 3 | 4 | 24 VDC SI | 5069-IB8S
458 |  | RL7-CKR-101-ZSS-05 | PRS306021 | JIC9B,OS9A | COOKER 1 COLUMN DUMPER SAFETY GATE ACTIVE SAFETY INPUT CH2 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 3 | 5 | 24 VDC SI | 5069-IB8S
459 |  | RL7-MLT-107.M1 |  |  | COOKER 1 COLUMN DUMPER ENABLE | DG7020 | MCC | RL7-INTSL-RIO1 | 18 | 14 | 0 | 24 VDC DO | 5069-OB16
460 | RL7-MTL-107-PB-01 | RL7-MLT-107-PB-01 | PB505011 | JIC7B | COOKER 1 DUMPER E-STOP SAFETY INPUT CH1 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 1 | 0 | 24 VDC SI | 5069-IB8S
461 | RL7-MTL-107-PB-01 | RL7-MLT-107-PB-01 | PB505011 | JIC7B | COOKER 1 DUMPER E-STOP SAFETY INPUT CH2 | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 1 | 1 | 24 VDC SI | 5069-IB8S
462 | RL7-MLT-107-PB-02 | RL7-MLT-107-PB-02 | PB506031 | JIC7B | COOKER 1 DUMPER STOP PB | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 6 | 2 | 24 VDC DI | 5069-IB16
463 | RL7-MLT-107-PB-03 | RL7-MLT-107-PB-03 | PB506021 | JIC7B | COOKER 1 DUMPER DOWN PB | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 6 | 3 | 24 VDC DI | 5069-IB16
464 | RL7-MLT-107-PB-04 | RL7-MLT-107-PB-04 | PB506011 | JIC7B | COOKER 1 DUMPER UP PB | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 6 | 4 | 24 VDC DI | 5069-IB16
465 | RL7-MTL-107-PBL-01 | RL7-MLT-107-PBL-01 | PB505011 | JIC7B | COOKER 1 DUMPER E-STOP PB PILOT LIGHT | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 8 | 0 | 24 VDC DO | 5069-OB16
466 |  | RL7-MLT-107-PL-01G |  |  | COOKER 1 DUMPER GREEN PILOT LIGHT | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 8 | 3 | 24 VDC DO | 5069-OB16
467 |  | RL7-MLT-107-PL-01R |  |  | COOKER 1 DUMPER RED PILOT LIGHT | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 8 | 1 | 24 VDC DO | 5069-OB16
468 |  | RL7-MLT-107-PL-01Y |  |  | COOKER 1 DUMPER YELLOW PILOT LIGHT | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 8 | 2 | 24 VDC DO | 5069-OB16
469 | RL7-MLT-107-ZSC-01 | RL7-MLT-107-ZSC-01 | PRS506111 | JIC7B | COOKER 1 DUMPER DOWN POSITION | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 5 | 5 | 24 VDC DI | 5069-IB16
470 | RL7-MLT-107-ZSC-02 | RL7-MLT-107-ZSC-02 | PRS506091 | JIC7B | COOKER 1 DUMPER UP POSITION | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 5 | 4 | 24 VDC DI | 5069-IB16
471 | RL7-MLT-107-ZSC-03 | RL7-MLT-107-ZSC-03 | PRS506071 | JIC7B | COOKER 1 DUMPER OVERTRAVEL | DG7020 | PROC | RL7-CKR1-RIO1 | 12 | 5 | 3 | 24 VDC DI | 5069-IB16
472 | RL7-SKD-102-FIT-01 | RL7-SKD-102-FIT-01 |  |  | COOKER 1 LACTIC ACID FLOW | DG7020 | INTSL | RL7-INTSL-RIO2 | 19 | 11 | 0 | 4-20 mA AI | 5069-IF8 | 0 - 100%
473 | RL7-SKD-102-FIT-02 | RL7-SKD-102-FIT-02 |  |  | COOKER 2 LACTIC ACID FLOW | DG7020 | INTSL | RL7-INTSL-RIO2 | 19 | 11 | 1 | 4-20 mA AI | 5069-IF8
474 | RL7-SKD-102-XV-01 | RL7-SKD-102-XV-01 |  |  | COOKER 1 LACTIC ACID SUPPLY VALVE OPEN SOLENOID | DG7020 | INTSL | RL7-INTSL-RIO2 | 19 | 7 | 0 | 24 VDC DO | 5069-OB16
475 | RL7-SKD-102-XV-02 | RL7-SKD-102-XV-02 |  |  | COOKER 2 LACTIC ACID SUPPLY VALVE OPEN SOLENOID | DG7020 | INTSL | RL7-INTSL-RIO2 | 19 | 7 | 1 | 24 VDC DO | 5069-OB16
476 | RL7-SKD-102-ZSC-01 | RL7-SKD-102-ZSC-01 |  |  | COOKER 1 LACTIC ACID SUPPLY VALVE CLOSE LIMIT SWITCH | DG7020 | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 5 | 24 VDC DI | 5069-IB16
477 | RL7-SKD-102-ZSC-02 | RL7-SKD-102-ZSC-02 |  |  | COOKER 2 LACTIC ACID SUPPLY VALVE CLOSE LIMIT SWITCH | DG7020 | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 7 | 24 VDC DI | 5069-IB16
478 | RL7-SKD-102-ZSO-01 | RL7-SKD-102-ZSO-01 |  |  | COOKER 1 LACTIC ACID SUPPLY VALVE OPEN LIMIT SWITCH | DG7020 | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 4 | 24 VDC DI | 5069-IB16
479 | RL7-SKD-102-ZSO-02 | RL7-SKD-102-ZSO-02 |  |  | COOKER 2 LACTIC ACID SUPPLY VALVE OPEN LIMIT SWITCH | DG7020 | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 6 | 24 VDC DI | 5069-IB16
480 | RL7-MTL-108-PB-01 | RL7-MLT-108-PB-01 | PB605011 | JIC8B | COOKER 2 DUMPER E-STOP PUSHBUTTON CH1 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 1 | 0 | 24 VDC SI | 5069-IB8S
481 | RL7-MTL-108-PB-01 | RL7-MLT-108-PB-01 | PB605011 | JIC8B | COOKER 2 DUMPER E-STOP PUSHBUTTON CH2 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 1 | 1 | 24 VDC SI | 5069-IB8S
482 |  | RL7-CKR-102-PB-02 |  |  | COOKERS PLATFORM E-STOP PUSHBUTTON CH1 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 1 | 2 | 24 VDC SI | 5069-IB8S
483 |  | RL7-CKR-102-PB-02 |  |  | COOKERS PLATFORM E-STOP PUSHBUTTON CH2 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 1 | 3 | 24 VDC SI | 5069-IB8S
484 | RL7-CKR-102-ZSS-03 | RL7-CKR-102-ZSS-03 | PRS406091 |  | COOKER 2 MIXER HATCH CLOSED RFID POSITION SWITCH CH1 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 1 | 4 | 24 VDC SI | 5069-IB8S
485 | RL7-CKR-102-ZSS-03 | RL7-CKR-102-ZSS-03 | PRS406091 |  | COOKER 2 MIXER HATCH CLOSED RFID POSITION SWITCH CH2 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 1 | 5 | 24 VDC SI | 5069-IB8S
486 | RL7-CKR-102-ZSS-02 | RL7-CKR-102-ZSS-02 | PRS406021 |  | COOKER 2 MIXER COVER CLOSED RFID POSITION SWITCH CH1 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 2 | 0 | 24 VDC SI | 5069-IB8S
487 | RL7-CKR-102-ZSS-02 | RL7-CKR-102-ZSS-02 | PRS406021 |  | COOKER 2 MIXER COVER CLOSED RFID POSITION SWITCH CH2 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 2 | 1 | 24 VDC SI | 5069-IB8S
488 | RL7-CKR-102-PB-01 | RL7-CKR-102-PB-01 |  |  | COOKER 2 E-STOP PB SAFETY INPUT CH1 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 2 | 2 | 24 VDC SI | 5069-IB8S
489 | RL7-CKR-102-PB-01 | RL7-CKR-102-PB-01 |  |  | COOKER 2 E-STOP PB SAFETY INPUT CH2 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 2 | 3 | 24 VDC SI | 5069-IB8S
490 | RL7-CKR-102-ZSS-01 | RL7-CKR-102-ZSS-01 | PRS406061 |  | COOKER 2 SAFETY GRATE RFID POSITION SWITCH CH1 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 2 | 4 | 24 VDC SI | 5069-IB8S
491 | RL7-CKR-102-ZSS-01 | RL7-CKR-102-ZSS-01 | PRS406061 |  | COOKER 2 SAFETY GRATE RFID POSITION SWITCH CH2 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 2 | 5 | 24 VDC SI | 5069-IB8S
492 | RL7-CKR-102-ZSS-23A | RL7-CKR-102-ZSC-23A | SOL406171 | JIC6B | COOKER 2 SAFETY AIR DUMP SOLENOID A STATUS | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 2 | 6 | 24 VDC SI | 5069-IB8S
493 | RL7-CKR-102-ZSS-23A | RL7-CKR-102-ZSC-23B | SOL406171 | JIC6B | COOKER 2 SAFETY AIR DUMP SOLENOID B STATUS | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 2 | 7 | 24 VDC SI | 5069-IB8S
494 | RL7-MTL-108-PB-01 | RL7-CKR-102-PB-03 | PB505161 | OS7C | COOKER 2 COLUMN DUMPER ENTRY REQUEST PB | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 3 | 0 | 24 VDC SI | 5069-IB8S
495 | RL7-MTL-108-PB-01 | RL7-CKR-102-PB-04 | PB505191 | OS7C | COOKER 2 COLUMN DUMPER RESET GATE LOCK PB | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 3 | 1 | 24 VDC SI | 5069-IB8S
496 |  | RL7-CKR-102-ZSS-04 | PRS306021 | OS9A/JIC9B | COOKER 2 COLUMN DUMPER IN DOWN POSITION SAFETY INPUT 1 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 3 | 2 | 24 VDC SI | 5069-IB8S
497 |  | RL7-CKR-102-ZSS-04 | PRS306021 | OS9A/JIC9B | COOKER 2 COLUMN DUMPER IN DOWN POSITION SAFETY INPUT 2 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 3 | 3 | 24 VDC SI | 5069-IB8S
498 | RL7-CKR-102-ZSS-03 | RL7-CKR-102-ZSS-05 | PRS306021 | OS9A/JIC9B | COOKER 2 COLUMN DUMPER SAFETY GATE ACTIVE SAFETY INPUT 1 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 3 | 4 | 24 VDC SI | 5069-IB8S
499 | RL7-CKR-102-ZSS-03 | RL7-CKR-102-ZSS-05 | PRS306021 | OS9A/JIC9B | COOKER 2 COLUMN DUMPER SAFETY GATE ACTIVE SAFETY INPUT 2 | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 3 | 5 | 24 VDC SI | 5069-IB8S
500 | RL7-CKR-102-XYS-23A | RL7-CKR-102-XYS-23A | SOL406171 | JIC6B | COOKER 2 SAFETY AIR DUMP SOLENOID A | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 4 | 0 | 24 VDC SO | 5069-OBV8S
501 | RL7-CKR-102-XYS-23B | RL7-CKR-102-XYS-23B | SOL406171 | JIC6B | COOKER 2 SAFETY AIR DUMP SOLENOID B | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 4 | 1 | 24 VDC SO | 5069-OBV8S
502 | RL7-CKR-102-ZSC-21 | RL7-CKR-102-ZSC-21 | PRS407211 |  | COOKER 2 LOCKBAR ENGAGED | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 0 | 24 VDC DI | 5069-IB16
503 | RL7-CKR-102-ZSO-21 | RL7-CKR-102-ZSO-21 | PRS407231 |  | COOKER 2 LOCKBAR RELEASED | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 1 | 24 VDC DI | 5069-IB16
504 | RL7-CKR-102-PSL-01 | RL7-CKR-102-PSL-01 | PRG407011 | JIB6B | COOKER 2 REGULATOR LOW PRESSURE SWITCH | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 2 | 24 VDC DI | 5069-IB16
505 | RL7-MLT-108-ZSC-03 | RL7-MLT-108-ZSC-03 | PRS606071 | JIB8B | COOKER 2 DUMPER OVERTRAVEL | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 3 | 24 VDC DI | 5069-IB16
506 | RL7-MLT-108-ZSC-02 | RL7-MLT-108-ZSC-02 | PRS606091 | JIB8B | COOKER 2 DUMPER UP POSITION | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 4 | 24 VDC DI | 5069-IB16
507 | RL7-MLT-108-ZSC-01 | RL7-MLT-108-ZSC-01 | PRS606111 | JIB8B | COOKER 2 DUMPER DOWN POSITION | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 5 | 24 VDC DI | 5069-IB16
508 | RL7-CKR-102-ZSO-22 | RL7-CKR-102-ZSO-22 | PRS407191 | JIB8B | COOKER 2 COVER OPEN | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 6 | 24 VDC DI | 5069-IB16
509 |  | RL7-CKR-102-PBL-03 | PB505161 | OS7C | COOKER 2 COLUMN DUMPER ENTRY REQUEST PB PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 7 | 24 VDC DI | 5069-IB16
510 |  | RL7-CKR-102-PBL-04 | PB505191 | OS7C | COOKER 2 COLUMN DUMPER RESET GATE LOCK PB PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 5 | 8 | 24 VDC DI | 5069-IB16
511 | RL7-CKR-102-ZSO-20 | RL7-CKR-102-ZSO-20 | VLV307261 |  | COOKER 2 SAFETY GRATE RELEASED | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 6 | 0 | 24 VDC DI | 5069-IB16
512 | RL7-CKR-102-ZSC-20 | RL7-CKR-102-ZSC-20 | VLV307261 |  | COOKER 2 SAFETY GRATE ENGAGED | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 6 | 1 | 24 VDC DI | 5069-IB16
513 | RL7-MLT-108-PB-04 | RL7-MLT-108-PB-04 | PB606031 | JIC8B | COOKER 2 DUMPER STOP PB | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 6 | 2 | 24 VDC DI | 5069-IB16
514 | RL7-MLT-108-PB-03 | RL7-MLT-108-PB-03 | PB606021 | JIC8B | COOKER 2 DUMPER DOWN PB | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 6 | 3 | 24 VDC DI | 5069-IB16
515 | RL7-MLT-108-PB-02 | RL7-MLT-108-PB-02 | PB606011 | JIC8B | COOKER 2 DUMPER UP PB | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 6 | 4 | 24 VDC DI | 5069-IB16
516 | RL7-CKR-102-ZSO-18 | RL7-CKR-102-ZSO-18 | PRS407111 |  | COOKER 2 LEFT DISCHARGE VALVE OPEN | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 6 | 6 | 24 VDC DI | 5069-IB16
517 | RL7-CKR-102-ZSC-18 | RL7-CKR-102-ZSC-18 | PRS407111 |  | COOKER 2 LEFT DISCHARGE VALVE CLOSE | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 6 | 7 | 24 VDC DI | 5069-IB16
518 | RL7-CKR-102-ZSO-19 | RL7-CKR-102-ZSO-19 | PRS407131 |  | COOKER 2 RIGHT DISCHARGE VALVE OPEN | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 6 | 8 | 24 VDC DI | 5069-IB16
519 | RL7-CKR-102-ZSC-19 | RL7-CKR-102-ZSC-19 | PRS407131 |  | COOKER 2 RIGHT DISCHARGE VALVE CLOSE | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 6 | 9 | 24 VDC DI | 5069-IB16
520 | RL7-MTL-108-PBL-01 | RL7-MLT-108-PBL-01 | PB605011 | JIC8B | COOKER 2 DUMPER E-STOP PB PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 8 | 0 | 24 VDC DO | 5069-OB16
521 |  | RL7-MLT-108-PL-01R |  |  | COOKER 2 DUMPER RED PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 8 | 1 | 24 VDC DO | 5069-OB16
522 |  | RL7-MLT-108-PL-01Y |  |  | COOKER 2 DUMPER YELLOW PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 8 | 2 | 24 VDC DO | 5069-OB16
523 |  | RL7-MLT-108-PL-01G |  |  | COOKER 2 DUMPER GREEN PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 8 | 3 | 24 VDC DO | 5069-OB16
524 | RL7-CKR-102-PBL-01 | RL7-CKR-102-PBL-02 |  |  | COOKER 2 E-STOP PB PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 8 | 4 | 24 VDC DO | 5069-OB16
525 | RL7-CKR-102-PL-01R | RL7-CKR-102-PL-01R |  |  | COOKER 2 RED PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 8 | 5 | 24 VDC DO | 5069-OB16
526 | RL7-CKR-102-PL-01Y | RL7-CKR-102-PL-01Y |  |  | COOKER 2 YELLOW PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 8 | 6 | 24 VDC DO | 5069-OB16
527 | RL7-CKR-102-PL-01G | RL7-CKR-102-PL-01G |  |  | COOKER 2 GREEN PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 8 | 7 | 24 VDC DO | 5069-OB16
528 |  | RL7-CKR-102-PBL-02 |  |  | COOKERS PLATFORM E-STOP PB PILOT LIGHT | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 8 | 14 | 24 VDC DO | 5069-OB16
529 | RL7-CKR-102-XY-22A | RL7-CKR-102-XY-22A | SOL407041 | JIC6B | COOKER 2 COVER OPEN SOLENOID | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 0 | 24 VDC DO | 5069-OB16
530 | RL7-CKR-102-XY-22B | RL7-CKR-102-XY-22B | SOL407041 | JIC6B | COOKER 2 COVER CLOSE SOLENOID | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 1 | 24 VDC DO | 5069-OB16
531 | RL7-CKR-102-XY-20A | RL7-CKR-102-XY-20A | SOL407061 | JIC6B | COOKER 2 SAFETY GRATE ENGAGE SOLENOID | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 2 | 24 VDC DO | 5069-OB16
532 | RL7-CKR-102-XY-20B | RL7-CKR-102-XY-20B | SOL407061 | JIC6B | COOKER 2 SAFETY GRATE RELEASE SOLENOID | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 3 | 24 VDC DO | 5069-OB16
533 | RL7-CKR-102-XY-18A | RL7-CKR-102-XY-18A | SOL407071 | JIC6B | COOKER 2 LEFT DISCHARGE VALVE OPEN SOLENOID | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 4 | 24 VDC DO | 5069-OB16
534 | RL7-CKR-102-XY-18B | RL7-CKR-102-XY-18B | SOL407071 | JIC6B | COOKER 2 LEFT DISCHARGE VALVE CLOSE SOLENOID | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 5 | 24 VDC DO | 5069-OB16
535 | RL7-CKR-102-XY-19A | RL7-CKR-102-XY-19A | SOL407161 | JIC6B | COOKER 2 RIGHT DISCHARGE VALVE OPEN SOLENOID | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 6 | 24 VDC DO | 5069-OB16
536 | RL7-CKR-102-XY-19B | RL7-CKR-102-XY-19B | SOL407161 | JIC6B | COOKER 2 RIGHT DISCHARGE VALVE CLOSE SOLENOID | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 7 | 24 VDC DO | 5069-OB16
537 | RL7-CNV-106-XV-08 | RL7-CKR-102-XY-24 |  |  | COOKER 2 AIR PURGE SOLENOID VALVE | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 10 | 24 VDC DO | 5069-OB16
538 | RL7-CKR-102-TIT-01 | RL7-CKR-102-TIT-01 |  |  | COOKER 2 MIXER SIDE TEMPERATURE TRANSMITTER | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 10 | 0 | 4-20 mA AI | 5069-IF8
539 | RL7-CKR-102-TIT-02 | RL7-CKR-102-TIT-02 |  |  | COOKER 2 MIXER SIDE TEMPERATURE TRANSMITTER | DG7021 | PROC | RL7-CKR2-RIO1 | 13 | 10 | 1 | 4-20 mA AI | 5069-IF8
540 | RL7-CKR-102-ZSO-25 | RL7-CKR-102-ZSO-25 |  |  | COOKER 2 CIPS MIX PROOF VALVE OPEN LIMIT SWITCH | DG7021 | INTSL | RL7-INTSL-RIO1 | 18 | 2 | 0 | 24 VDC DI | 5069-IB16
541 | RL7-CKR-102-ZSC-25 | RL7-CKR-102-ZSC-25 |  |  | COOKER 2 CIPS MIX PROOF VALVE CLOSED LIMIT SWITCH | DG7021 | INTSL | RL7-INTSL-RIO1 | 18 | 2 | 1 | 24 VDC DI | 5069-IB16
542 | RL7-CKR-102-XV-25 | RL7-CKR-102-XV-25 |  |  | COOKER 2 CIPS MIX PROOF VALVE OPEN SOLENOID | DG7021 | INTSL | RL7-INTSL-RIO1 | 18 | 4 | 2 | 24 VDC DO | 5069-OB16
543 | RL7-CKR-102-FVI-02 | RL7-CKR-102-FVI-02 |  |  | COOKER 2 CIPS CONTROL VALVE POSITION FEEDBACK | DG7021 | INTSL | RL7-INTSL-RIO1 | 18 | 7 | 4 | 4-20 mA AI | 5069-IF8
544 | RL7-CKR-102-FIT-02 | RL7-CKR-102-FIT-02 |  |  | COOKER 2 CIPS FLOW | DG7021 | INTSL | RL7-INTSL-RIO1 | 18 | 10 | 2 | 4-20 mA AI | 5069-IF8 | 0 - 300 GPM
545 | RL7-CKR-102-FCV-02 | RL7-CKR-102-FCV-02 |  |  | COOKER 2 CONTROL VALVE | DG7021 | INTSL | RL7-INTSL-RIO1 | 18 | 13 | 2 | 4-20 mA AO | 5069-OF8
546 |  | RL7-MLT-108.M1 |  |  | COOKER 2 COLUMN DUMPER ENABLE | DG7021 | MCC | RL7-INTSL-RIO1 | 18 | 14 | 1 | 24 VDC DO | 5069-OB16
547 | RL7-CKR-101-XY-02 | RL7-CKR-101-XV-02 | SOL307091 | JIC5B | COOKER 1 STEAM VALVES 1-8 | DG7022 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 8 | 24 VDC DO | 5069-OB16
548 | RL7-CKR-101-XY-10 | RL7-CKR-101-XV-10 | SOL307101 | JIC5B | COOKER 1 STEAM VALVES 9-16 | DG7022 | PROC | RL7-CKR1-RIO1 | 12 | 9 | 9 | 24 VDC DO | 5069-OB16
549 | RL7-CKR-102-XY-02 | RL7-CKR-102-XV-02 | SOL407091 | JIC6B | COOKER 2 STEAM VALVES 1-8 | DG7022 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 8 | 24 VDC DO | 5069-OB16
550 | RL7-CKR-102-XY-10 | RL7-CKR-102-XV-10 | SOL407101 | JIC6B | COOKER 2 STEAM VALVES 9-16 | DG7022 | PROC | RL7-CKR2-RIO1 | 13 | 9 | 9 | 24 VDC DO | 5069-OB16
551 | RL7-PMP-104-ZSO-01 | RL7-PMP-104-ZSO-01 |  |  | COOKER 1 PRODUCT TO METAL DETECTOR VALVE OPEN LIMIT SWITCH | DG7023 | INTSL | RL7-INTSL-RIO1 | 18 | 1 | 6 | 24 VDC DI | 5069-IB16
552 | RL7-PMP-104-ZSC-01 | RL7-PMP-104-ZSC-01 |  |  | COOKER 1 PRODUCT TO METAL DETECTOR VALVE CLOSED LIMIT SWITCH | DG7023 | INTSL | RL7-INTSL-RIO1 | 18 | 1 | 7 | 24 VDC DI | 5069-IB16
553 | RL7-MDT-102-ZSO-02 | RL7-MDT-102-ZSO-02 |  |  | PIPELINE METAL DETECTOR PRODUCT SUPPLY VALVE OPEN LIMIT SWITCH | DG7023 | INTSL | RL7-INTSL-RIO1 | 18 | 1 | 8 | 24 VDC DI | 5069-IB16
554 | RL7-MDT-102-ZSC-02 | RL7-MDT-102-ZSC-02 |  |  | PIPELINE METAL DETECTOR PRODUCT SUPPLY VALVE CLOSED LIMIT SWITCH | DG7023 | INTSL | RL7-INTSL-RIO1 | 18 | 1 | 9 | 24 VDC DI | 5069-IB16
555 | RL7-PMP-105-ZSO-01 | RL7-PMP-105-ZSO-01 |  |  | COOKER 2 PRODUCT TO METAL DETECTOR VALVE OPEN LIMIT SWITCH | DG7023 | INTSL | RL7-INTSL-RIO1 | 18 | 2 | 6 | 24 VDC DI | 5069-IB16
556 | RL7-PMP-105-ZSC-01 | RL7-PMP-105-ZSC-01 |  |  | COOKER 2 PRODUCT TO METAL DETECTOR VALVE CLOSED LIMIT SWITCH | DG7023 | INTSL | RL7-INTSL-RIO1 | 18 | 2 | 7 | 24 VDC DI | 5069-IB16
557 | RL7-PMP-104-XV-01 | RL7-PMP-104-XV-01 |  |  | COOKER 1 PRODUCT TO MTD VALVE OPEN SOLENOID | DG7023 | INTSL | RL7-INTSL-RIO1 | 18 | 3 | 3 | 24 VDC DO | 5069-OB16
558 | RL7-PMP-105-XV-01 | RL7-PMP-105-XV-01 |  |  | COOKER 2 PRODUCT TO MTD VALVE OPEN SOLENOID | DG7023 | INTSL | RL7-INTSL-RIO1 | 18 | 4 | 3 | 24 VDC DO | 5069-OB16
559 | RL7-AGC-201-ZSS-01 | RL7-AGC-201-ZSS-01 | PRS1106021 |  | DISCHARGE AUGER CART SAFETY GRATE RFID POSITION SWITCH SAFETY INPUT CH1 | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 1 | 0 | 24 VDC SI | 5069-IB8S
560 | RL7-AGC-201-ZSS-01 | RL7-AGC-201-ZSS-01 | PRS1106021 |  | DISCHARGE AUGER CART SAFETY GRATE RFID POSITION SWITCH SAFETY INPUT CH2 | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 1 | 1 | 24 VDC SI | 5069-IB8S
561 | RL7-AGC-201-ZSS-03 | RL7-AGC-201-ZSS-03 | PRS1106061 |  | DISCHARGE AUGER CART PRESSURE TUBE RFID POSITION SWITCH SAFETY INPUT CH1 | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 1 | 2 | 24 VDC SI | 5069-IB8S
562 | RL7-AGC-201-ZSS-03 | RL7-AGC-201-ZSS-03 | PRS1106061 |  | DISCHARGE AUGER CART PRESSURE TUBE RFID POSITION SWITCH SAFETY INPUT CH2 | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 1 | 3 | 24 VDC SI | 5069-IB8S
563 | RL7-AGC-201-PB-01 | RL7-AGC-201-PB-01 | PB1106191 | OS13A | DISCHARGE AUGER CART E-STOP PUSHBUTTON SAFETY INPUT CH1 | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 1 | 4 | 24 VDC SI | 5069-IB8S
564 | RL7-AGC-201-PB-01 | RL7-AGC-201-PB-01 | PB1106191 | OS13A | DISCHARGE AUGER CART E-STOP PUSHBUTTON SAFETY INPUT CH1 | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 1 | 5 | 24 VDC SI | 5069-IB8S
565 | RL7-AGC-201-ZSC-04A | RL7-AGC-201-ZSC-04A | SOL1106251 | JIC13B | DISCHARGE AUGER CART SAFETY AIR DUMP SOLENOID STATUS SAFETY INPUT CH1 | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 2 | 2 | 24 VDC SI | 5069-IB8S
566 | RL7-AGC-201-ZSC-04B | RL7-AGC-201-ZSC-04B | SOL1106251 | JIC13B | DISCHARGE AUGER CART SAFETY AIR DUMP SOLENOID STATUS SAFETY INPUT CH2 | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 2 | 3 | 24 VDC SI | 5069-IB8S
567 | RL7-AGC-201-XYS-04A | RL7-AGC-201-XYS-04A | SOL1106251A | JIC13B | DISCHARGE AUGER CART SAFETY AIR DUMP SOLENOID A | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 3 | 0 | 24 VDC SO | 5069-OBV8S
568 | RL7-AGC-201-XYS-04B | RL7-AGC-201-XYS-04B | SOL1106251B | JIC13B | DISCHARGE AUGER CART SAFETY AIR DUMP SOLENOID B | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 3 | 1 | 24 VDC SO | 5069-OBV8S
569 | RL7-AGC-201-ZSC-01 | RL7-AGC-201-ZSC-01 | PRS1107151 |  | DISCHARGE AUGER CART LOCKBAR ENGAGED | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 4 | 0 | 24 VDC DI | 5069-IB16
570 | RL7-AGC-201-ZSO-01 | RL7-AGC-201-ZSO-01 | PRS1107171 |  | DISCHARGE AUGER CART LOCKBAR RELEASED | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 4 | 1 | 24 VDC DI | 5069-IB16
571 |  | RL7-AGC-201-HS-01A | SS1107221 | OS13A | DISCHARGE AUGER CART OPEN COVER SELECTOR SWITCH | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 4 | 6 | 24 VDC DI | 5069-IB16
572 |  | RL7-AGC-201-HS-01B | SS1107221 | OS13A | DISCHARGE AUGER CART CLOSE COVER SELECTOR SWITCH | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 4 | 7 | 24 VDC DI | 5069-IB16
573 | RL7-AGC-201-HS-01A | RL7-AGC-201-PB-02 | PB1107241 | OS13A | DISCHARGE AUGER CART PUMP JOG PUSHBUTTON | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 4 | 8 | 24 VDC DI | 5069-IB16
574 | RL7-AGC-201-ZSC-01 | RL7-AGC-201-ZSO-08 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE TO CIP SKID IN PROCESS POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 5 | 0 | 24 VDC DI | 5069-IB16
575 | RL7-AGC-201-ZSO-01 | RL7-AGC-201-ZSC-08 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE TO CIP SKID IN SANITATION POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 5 | 1 | 24 VDC DI | 5069-IB16
576 | RL7-AGC-201-PSL-01 | RL7-AGC-201-ZSO-09 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE TO ROLLS MACHINE IN PROCESS POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 5 | 2 | 24 VDC DI | 5069-IB16
577 | RL7-AGC-201-ZSC-03 | RL7-AGC-201-ZSC-09 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE TO ROLLS MACHINE IN SANITATION POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 5 | 3 | 24 VDC DI | 5069-IB16
578 | RL7-AGC-201-ZSC-04 | RL7-AGC-201-ZSO-10 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE TO CIP SKID IN SNITATION POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 5 | 4 | 24 VDC DI | 5069-IB16
579 |  | RL7-AGC-201-ZSC-10 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE TO CIP SKID IN PROCESS POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 5 | 5 | 24 VDC DI | 5069-IB16
580 |  | RL7-AGC-201-ZSO-11 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE FROM PIPELINE MAGNET IN PROCESS POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 5 | 6 | 24 VDC DI | 5069-IB16
581 |  | RL7-AGC-201-ZSC-11 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE FROM PIPELINE MAGNET IN SANITATION POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 5 | 7 | 24 VDC DI | 5069-IB16
582 | RL7-AGC-201-HS-01A | RL7-AGC-201-ZSO-25 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE FROM CIP SKID IN SNITATION POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 5 | 8 | 24 VDC DI | 5069-IB16
583 | RL7-AGC-201-HS-01B | RL7-AGC-201-ZSC-25 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE FROM CIP SKID IN PROCESS POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 5 | 9 | 24 VDC DI | 5069-IB16
584 | RL7-AGC-201-PBL-01 | RL7-AGC-201-PBL-01 | PB1106191 | OS13A | DISCHARGE AUGER CART E-STOP PB PILOT LIGHT | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 0 | 24 VDC DO | 5069-OB16
585 | RL7-AGC-201-XY-02 | RL7-AGC-201-XY-02A | SOL1107021 | JIC13B | DISCHARGE AUGER CART COVER OPEN SOLENOID | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 2 | 24 VDC DO | 5069-OB16
586 | RL7-AGC-201-XY-02 | RL7-AGC-201-XY-02B | SOL1107021 | JIC13B | DISCHARGE AUGER CART COVER CLOSE SOLENOID | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 3 | 24 VDC DO | 5069-OB16
587 |  | RL7-AGC-201-XV-08 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE TO CIP SKID IN PROCESS POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 4 | 24 VDC DO | 5069-OB16
588 |  | RL7-AGC-201-XV-09 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE TO ROLLS MACHINE IN PROCESS POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 5 | 24 VDC DO | 5069-OB16
589 |  | RL7-AGC-201-XV-10 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE TO CIP SKID IN PROCESS POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 6 | 24 VDC DO | 5069-OB16
590 |  | RL7-AGC-201-XV-11 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE FROM PIPELINE MAGNET IN PROCESS POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 7 | 24 VDC DO | 5069-OB16
591 |  | RL7-AGC-201-XV-25 |  |  | DISCHARGE AUGER CART MIX PROOF VALVE FROM CIP SKID IN PROCESS POSITION | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 8 | 24 VDC DO | 5069-OB16
592 | RL7-AGC-201-AH-01 | RL7-AGC-201-AH-01 |  |  | DISCHARGE AUGER CART ALARM HORN | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 12 | 24 VDC DO | 5069-OB16
593 | RL7-AGC-201-PL-01R | RL7-AGC-201-PL-01R |  |  | DISCHARGE AUGER CART RED PILOT LIGHT | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 13 | 24 VDC DO | 5069-OB16
594 | RL7-AGC-201-PL-01Y | RL7-AGC-201-PL-01Y |  |  | DISCHARGE AUGER CART YELLOW PILOT LIGHT | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 14 | 24 VDC DO | 5069-OB16
595 | RL7-AGC-201-PL-01G | RL7-AGC-201-PL-01G |  |  | DISCHARGE AUGER CART GREEN PILOT LIGHT | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 7 | 15 | 24 VDC DO | 5069-OB16
596 | RL7-AGC-201-TIT-01 | RL7-AGC-201-FIT-02 |  |  | DISCHARGE AUGER CART CIPS FLOW | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 8 | 0 | 4-20 mA AI | 5069-IF8
597 | RL7-AGC-201-TIT-02 | RL7-AGC-201-FVI-02 |  |  | DISCHARGE AUGER CART CIPS CONTROL VALVE POSITION FEEDBACK | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 8 | 1 | 4-20 mA AI | 5069-IF8
598 |  | RL7-AGC-201-TIT-01 |  |  | DISCHARGE AUGER CART SIDE TEMPERATURE TRANSMITTER | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 8 | 2 | 4-20 mA AI | 5069-IF8
599 |  | RL7-AGC-201-TIT-02 |  |  | DISCHARGE AUGER CART SIDE TEMPERATURE TRANSMITTER | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 8 | 3 | 4-20 mA AI | 5069-IF8
600 |  | RL7-AGC-201-FCV-02 |  |  | DISCHARGE AUGER CART CIPS FLOW CONTROL VALVE | DG7030 | CHILL | RL7-DAGC1-RIO1 | 14 | 9 | 0 | 4-20 mA AO | 5069-OF8
601 | RL7-PMP-208-FVl-01 | RL7-PMP-208-FVl-01 |  |  | COOLING WATER JACKET CHR CONTROL VALVE POSITION FEEDBACK | DG7030 | INTSL | RL7-INTSL-RIO2 | 19 | 11 | 2 | 4-20 mA AI | 5069-IF8
602 | RL7-PMP-208-FCV-01 | RL7-PMP-208-FCV-01 |  |  | COOLING WATER JACKET CHR CONTROL VALVE | DG7030 | INTSL | RL7-INTSL-RIO2 | 19 | 13 | 3 | 4-20 mA AO | 5069-OF8
603 | RL7-CNV-204-PB-01 | RL7-CNV-204-PB-01 |  |  | SERPENTINE INFEED CONVEYOR #2 E-STOP SAFETY INPUT CH1 | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 1 | 4 | 24 VDC SI | 5069-IB8S
604 | RL7-CNV-204-PB-01 | RL7-CNV-204-PB-01 |  |  | SERPENTINE INFEED CONVEYOR #2 E-STOP SAFETY INPUT CH2 | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 1 | 5 | 24 VDC SI | 5069-IB8S
605 | RL7-CNV-204-ZEC-01 | RL7-CNV-204-ZEC-01 |  |  | INFEED COUNT PE | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 7 | 24 VDC DI | 5069-IB16
606 | RL7-CNV-204-ZEC-02 | RL7-CNV-204-ZEC-02 |  |  | CAM SWITCH | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 9 | 24 VDC DI | 5069-IB16
607 |  | RL7-CNV-204-PSL-01 |  |  | AIR PRESSURE GOOD | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 12 | 24 VDC DI | 5069-IB16
608 | RL7-CNV-204-PB-03 | RL7-CNV-204-PB-03 |  |  | INFEED LOADER JAM REMOVAL JOG PUSHBUTTON | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 4 | 2 | 24 VDC DI | 5069-IB16
609 | RL7-CNV-204-XY-01 | RL7-CNV-204-XY-01 |  |  | INFEED BRAKE 1 ADVANCE SOLENOID | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 4 | 24 VDC DO | 5069-OB16
610 | RL7-CNV-204-XY-02 | RL7-CNV-204-XY-02 |  |  | INFEED BRAKE 2 ADVANCE SOLENOID | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 6 | 24 VDC DO | 5069-OB16
611 | RL7-CNV-204-XY-03 | RL7-CNV-204-XY-03 |  |  | INFEED LOADER EXTEND SOLENOID | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 8 | 24 VDC DO | 5069-OB16
612 | RL7-CNV-204-XY-04 | RL7-CNV-204-XY-04 |  |  | INFEED LOADER RETRACT SOLENOID | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 9 | 24 VDC DO | 5069-OB16
613 | RL7-CNV-204-PBL-01 | RL7-CNV-204-PBL-01 |  |  | SERPENTINE INFEED CONVEYOR 2 E-STOP PB PILOT LIGHT | DG7032 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 14 | 24 VDC DO | 5069-OB16
614 |  | RL7-CNV-204-PB-02 |  |  | CHILLING PAUSE BUTTON | DG7032 | CHILL | RL7-INTSL-RIO2 | 19 | 3 | 11 | 24 VDC DI | 5069-IB16
615 | RL7-CHR-201-PB-02 | RL7-CHR-201-PB-01 |  |  | SERPENTINE E-STOP 1 SAFETY INPUT CH1 | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 1 | 2 | 24 VDC SI | 5069-IB8S
616 | RL7-CHR-201-PB-02 | RL7-CHR-201-PB-01 |  |  | SERPENTINE E-STOP 1 SAFETY INPUT CH2 | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 1 | 3 | 24 VDC SI | 5069-IB8S
617 | RL7-CHR-201-PB-04 | RL7-CHR-201-PB-02 |  |  | SERPENTINE E-STOP 2 SAFETY INPUT CH1 | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 1 | 6 | 24 VDC SI | 5069-IB8S
618 | RL7-CHR-201-PB-04 | RL7-CHR-201-PB-02 |  |  | SERPENTINE E-STOP 2 SAFETY INPUT CH2 | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 1 | 7 | 24 VDC SI | 5069-IB8S
619 | RL7-CHR-201-ZSC-01L | RL7-CHR-201-ZSC-01L |  |  | SERPENTINE CHILLER JAM SENSOR | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 0 | 24 VDC DI | 5069-IB16
620 | RL7-CHR-201-ZSC-02L | RL7-CHR-201-ZSC-02L |  |  | SERPENTINE CHILLER JAM SENSOR | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 1 | 24 VDC DI | 5069-IB16
621 | RL7-CHR-201-ZSC-03L | RL7-CHR-201-ZSC-03L |  |  | SERPENTINE CHILLER JAM SENSOR | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 2 | 24 VDC DI | 5069-IB16
622 | RL7-CHR-201-ZSC-01R | RL7-CHR-201-ZSC-01R |  |  | SERPENTINE CHILLER JAM SENSOR | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 3 | 24 VDC DI | 5069-IB16
623 | RL7-CHR-201-ZSC-02R | RL7-CHR-201-ZSC-02R |  |  | SERPENTINE CHILLER JAM SENSOR | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 4 | 24 VDC DI | 5069-IB16
624 | RL7-CHR-201-ZSC-03R | RL7-CHR-201-ZSC-03R |  |  | SERPENTINE CHILLER JAM SENSOR | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 5 | 24 VDC DI | 5069-IB16
625 | RL7-PMP-208-ZSO-01 | RL7-PMP-208-ZSO-01 |  |  | COOLING WATER JACKET CHS VALVE OPEN LIMIT SWITCH | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 14 | 24 VDC DI | 5069-IB16
626 | RL7-PMP-208-ZSC-01 | RL7-PMP-208-ZSC-01 |  |  | COOLING WATER JACKET CHS VALVE CLOSED LIMIT SWITCH | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 15 | 24 VDC DI | 5069-IB16
627 | RL7-FTR-205-ZSO-01 | RL7-FTR-205-ZSO-01 |  |  | SERPENTINE ZONE 2A FILTER PURGE VALVE OPEN LIMIT SWITCH | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 4 | 0 | 24 VDC DI | 5069-IB16
628 | RL7-FTR-205-ZSC-01 | RL7-FTR-205-ZSC-01 |  |  | SERPENTINE ZONE 2A FILTER PURGE VALVE CLOSED LIMIT SWITCH | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 4 | 1 | 24 VDC DI | 5069-IB16
629 | RL7-CHR-201-PL-01R | RL7-CHR-201-PL-01R |  |  | SERPENTINE RED STACK LIGHT | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 1 | 24 VDC DO | 5069-OB16
630 | RL7-CHR-201-PL-01Y | RL7-CHR-201-PL-01Y |  |  | SERPENTINE YELLOW STACK LIGHT | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 2 | 24 VDC DO | 5069-OB16
631 | RL7-CHR-201-PL-01G | RL7-CHR-201-PL-01G |  |  | SERPENTINE GREEN STACK LIGHT | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 3 | 24 VDC DO | 5069-OB16
632 | RL7-FTR-205-XV-01 | RL7-FTR-205-XV-01 |  |  | SERPENTINE ZONE 2A FILTER PURGE VALVE OPEN SOLENOID | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 10 | 24 VDC DO | 5069-OB16
633 | RL7-PMP-210-XC-01 | RL7-PMP-210-XC-01 |  |  | ZONE 1 DOSING PUMP REMOTE START / STOP | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 11 | 24 VDC DO | 5069-OB16
634 | RL7-PMP-209-XC-01 | RL7-PMP-209-XC-01 |  |  | ZONE 2 DOSING PUMP REMOTE START / STOP | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 12 | 24 VDC DO | 5069-OB16
635 | RL7-CHR-201-PBL-02 | RL7-CHR-201-PBL-01 |  |  | SERPENTINE E-STOP 1 PB LIGHT | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 13 | 24 VDC DO | 5069-OB16
636 | RL7-CHR-201-PBL-04 | RL7-CHR-201-PBL-02 |  |  | SERPENTINE E-STOP 2 PB LIGHT | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 5 | 15 | 24 VDC DO | 5069-OB16
637 | RL7-PMP-208-XV-01 | RL7-PMP-208-XV-01 |  |  | COOLING WATER JACKET CHS VALVE OPEN SOLENOID | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 6 | 3 | 24 VDC DO | 5069-OB16
638 | RL7-CHR-201-PIT-01 | RL7-CHR-201-PIT-01 |  |  | SERPENTINE ZONE 1 LEVEL | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 7 | 0 | 4-20 mA AI | 5069-IF8 | 0 - 1 PSI
639 | RL7-CHR-201-TIT-01 | RL7-CHR-201-TIT-01 |  |  | SERPENTINE ZONE 1 SUMP TEMPERATURE | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 7 | 1 | 4-20 mA AI | 5069-IF8
640 | RL7-PMP-203-PIT-01 | RL7-PMP-203-PIT-01 |  |  | SERPENTINE ZONE 1 CHR PRESSURE | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 7 | 2 | 4-20 mA AI | 5069-IF8 | 0 - 150 PSI
641 | RL7-PMP-204-PIT-01 | RL7-PMP-204-PIT-01 |  |  | SERPENTINE ZONE 2A RECIRC PRESSURE | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 7 | 3 | 4-20 mA AI | 5069-IF8 | 0 - 150 PSI
642 | RL7-CHR-201-PIT-02 | RL7-CHR-201-PIT-02 |  |  | SERPENTINE ZONE 2A LEVEL | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 7 | 4 | 4-20 mA AI | 5069-IF8 | 0 - 1 PSI
643 | RL7-CHR-201-TIT-02 | RL7-CHR-201-TIT-02 |  |  | SERPENTINE ZONE 2A SUMP TEMPERATURE | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 7 | 5 | 4-20 mA AI | 5069-IF8 | 0 - 100 F
644 | RL7-PMP-203-TIT-01 | RL7-PMP-203-TIT-01 |  |  | SERPENTINE ZONE 1 CHS TEMPERATURE | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 7 | 6 | 4-20 mA AI | 5069-IF8 | 0 - 100 F
645 |  | RL7-PMP-208-PIT-01 |  |  | COOLING WATER JACKET CHS PRESSURE | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 8 | 0 | 4-20 mA AI | 5069-IF8
646 |  | RL7-PMP-208-TIT-01 |  |  | COOLING WATER JACKET CHS TEMPERATURE | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 8 | 1 | 4-20 mA AI | 5069-IF8
647 | RL7-FTR-205-PT-01 | RL7-FTR-205-PT-01 |  |  | SERPENTINE ZONE 2A FILTER PURGE INLET PRESSURE | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 8 | 2 | 4-20 mA AI | 5069-IF8
648 | RL7-FTR-205-PT-02 | RL7-FTR-205-PT-02 |  |  | SERPENTINE ZONE 2A FILTER PURGE OUTLET PRESSURE | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 8 | 3 | 4-20 mA AI | 5069-IF8
649 | RL7-PMP-203-FIT-01 | RL7-PMP-203-FIT-01 |  |  | SERPENTINE ZONE 1 CHR FLOW | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 8 | 4 | 4-20 mA AI | 5069-IF8
650 | RL7-PMP-204-FIT-01 | RL7-PMP-204-FIT-01 |  |  | SERPENTINE ZONE 2A RECIRC FLOW | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 8 | 5 | 4-20 mA AI | 5069-IF8
651 | RL7-PMP-208-FIT-01 | RL7-PMP-208-FIT-01 |  |  | COOLING WATER JACKET CHS FLOW | DG7033 | CHILL | RL7-SERP-RIO1 | 15 | 8 | 6 | 4-20 mA AI | 5069-IF8
652 | RL7-CHR-201-PB-05 | RL7-CHR-201-PB-03 |  |  | SERPENTINE E-STOP 3 SAFETY INPUT CH1 | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 1 | 0 | 24 VDC SI | 5069-IB8S
653 | RL7-CHR-201-PB-05 | RL7-CHR-201-PB-03 |  |  | SERPENTINE E-STOP 3 SAFETY INPUT CH2 | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 1 | 1 | 24 VDC SI | 5069-IB8S
654 | RL7-CHR-201-PB-06 | RL7-CHR-201-PB-04 |  |  | SERPENTINE E-STOP 4 SAFETY INPUT CH1 | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 1 | 2 | 24 VDC SI | 5069-IB8S
655 | RL7-CHR-201-PB-06 | RL7-CHR-201-PB-04 |  |  | SERPENTINE E-STOP 4 SAFETY INPUT CH2 | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 1 | 3 | 24 VDC SI | 5069-IB8S
656 | RL7-CHR-201-PB-07 | RL7-CHR-201-PB-05 |  |  | SERPENTINE E-STOP 5 SAFETY INPUT CH1 | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 1 | 4 | 24 VDC SI | 5069-IB8S
657 | RL7-CHR-201-PB-07 | RL7-CHR-201-PB-05 |  |  | SERPENTINE E-STOP 5 SAFETY INPUT CH2 | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 1 | 5 | 24 VDC SI | 5069-IB8S
658 | RL7-CHR-201-ZSC-04L | RL7-CHR-201-ZSC-04L |  |  | SERPENTINE CHILLER JAM SENSOR | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 3 | 0 | 24 VDC DI | 5069-IB16
659 | RL7-FTR-207-ZSO-01 | RL7-FTR-207-ZSO-01 |  |  | SERPENTINE ZONE 2B FILTER PURGE VALVE OPEN LIMIT SWITCH | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 3 | 1 | 24 VDC DI | 5069-IB16
660 | RL7-FTR-207-ZSC-01 | RL7-FTR-207-ZSC-01 |  |  | SERPENTINE ZONE 2B FILTER PURGE VALVE CLOSED LIMIT SWITCH | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 3 | 2 | 24 VDC DI | 5069-IB16
661 | RL7-CHR-201-ZSC-04R | RL7-CHR-201-ZSC-04R |  |  | SERPENTINE CHILLER JAM SENSOR | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 3 | 3 | 24 VDC DI | 5069-IB16
662 | RL7-FTR-207-XV-01 | RL7-FTR-207-XV-01 |  |  | SERPENTINE ZONE 2B FILTER PURGE VALVE OPEN SOLENOID | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 5 | 11 | 24 VDC DO | 5069-OB16
663 | RL7-CHR-201-PBL-05 | RL7-CHR-201-PBL-03 |  |  | SERPENTINE E-STOP 3 PB LIGHT | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 5 | 12 | 24 VDC DO | 5069-OB16
664 | RL7-CHR-201-PBL-06 | RL7-CHR-201-PBL-04 |  |  | SERPENTINE E-STOP 4 PB LIGHT | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 5 | 13 | 24 VDC DO | 5069-OB16
665 | RL7-CHR-201-PBL-07 | RL7-CHR-201-PBL-05 |  |  | SERPENTINE E-STOP 5 PB LIGHT | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 5 | 14 | 24 VDC DO | 5069-OB16
666 | RL7-PMP-205-TIT-01 | RL7-PMP-205-TIT-01 |  |  | SERPENTINE ZONE 2A CHS TEMPERATURE | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 7 | 0 | 4-20 mA AI | 5069-IF8
667 | RL7-PMP-205-PIT-01 | RL7-PMP-205-PIT-01 |  |  | SERPENTINE ZONE 2A CHR PRESSURE | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 7 | 1 | 4-20 mA AI | 5069-IF8 | 0 - 150 PSI
668 | RL7-PMP-206-PIT-01 | RL7-PMP-206-PIT-01 |  |  | SERPENTINE ZONE 2B RECIRC PRESSURE | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 7 | 2 | 4-20 mA AI | 5069-IF8 | 0 - 150 PSI
669 | RL7-PMP-206-TIT-01 | RL7-PMP-206-TIT-01 |  |  | SERPENTINE ZONE 2B CHS TEMPERATURE | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 7 | 3 | 4-20 mA AI | 5069-IF8 | 0 - 100 F
670 | RL7-PMP-207-PIT-01 | RL7-PMP-207-PIT-01 |  |  | SERPENTINE ZONE 2B CHR PRESSURE | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 7 | 4 | 4-20 mA AI | 5069-IF8 | 0 - 150 PSI
671 | RL7-FTR-207-PT-01 | RL7-FTR-207-PT-01 |  |  | SERPENTINE ZONE 2B FILTER INLET PRESSURE | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 7 | 5 | 4-20 mA AI | 5069-IF8
672 | RL7-FTR-207-PT-02 | RL7-FTR-207-PT-02 |  |  | SERPENTINE ZONE 2B FILTER OUTLET PRESSURE | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 7 | 6 | 4-20 mA AI | 5069-IF8
673 | RL7-CHR-201-TIT-03 | RL7-CHR-201-TIT-03 |  |  | SERPENTINE ZONE 2B BASIN TEMPERATURE | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 7 | 7 | 4-20 mA AI | 5069-IF8
674 | RL7-PMP-205-FIT-01 | RL7-PMP-205-FIT-01 |  |  | SERPENTINE ZONE 2A CHR FLOW | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 8 | 0 | 4-20 mA AI | 5069-IF8 | 0 - 2425 GPM
675 | RL7-PMP-206-FIT-01 | RL7-PMP-206-FIT-01 |  |  | SERPENTINE ZONE 2B RECIRC FLOW | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 8 | 1 | 4-20 mA AI | 5069-IF8 | 0 - 2425 GPM
676 | RL7-PMP-207-FIT-01 | RL7-PMP-207-FIT-01 |  |  | SERPENTINE ZONE 2B CHR FLOW | DG7033 | CHILL | RL7-SERP-RIO2 | 16 | 8 | 2 | 4-20 mA AI | 5069-IF8 | 0 - 2425 GPM
677 | RL7-CHR-201-ZSC-03 | RL7-CHR-201-ZSO-03 |  |  | SERPENTINE ZONE 1 MAKEUP WATER VALVE OPEN LIMIT SWITCH | DG7033 | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 0 | 24 VDC DI | 5069-IB16
678 | RL7-CHR-201-ZSC-03 | RL7-CHR-201-ZSC-03 |  |  | SERPENTINE ZONE 1 MAKEUP WATER VALVE CLOSED LIMIT SWITCH | DG7033 | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 1 | 24 VDC DI | 5069-IB16
679 | RL7-CHR-201-ZSC-04 | RL7-CHR-201-ZSO-04 |  |  | SERPENTINE ZONE 2A MAKEUP WATER VALVE OPEN LIMIT SWITCH | DG7033 | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 2 | 24 VDC DI | 5069-IB16
680 | RL7-CHR-201-ZSC-04 | RL7-CHR-201-ZSC-04 |  |  | SERPENTINE ZONE 2A MAKEUP WATER VALVE CLOSED LIMIT SWITCH | DG7033 | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 3 | 24 VDC DI | 5069-IB16
681 | RL7-CNV-401-XY-01 | RL7-CHR-201-XV-03 |  |  | SERPENTINE ZONE 1 MAKEUP WATER VALVE OPEN SOLENOID | DG7033 | INTSL | RL7-INTSL-RIO2 | 19 | 7 | 2 | 24 VDC DO | 5069-OB16
682 | RL7-CNV-404-XY-01 | RL7-CHR-201-XV-04 |  |  | SERPENTINE ZONE 2A MAKEUP WATER VALVE OPEN SOLENOID | DG7033 | INTSL | RL7-INTSL-RIO2 | 19 | 7 | 3 | 24 VDC DO | 5069-OB16
683 | RL7-CHR-201-FVI-01 | RL7-CHR-201-FVI-01 |  |  | SERPENTINE ZONE 1 FLOW CONTROL VALVE POSITION FEEDBACK | DG7033 | HX / LA | RL7-INTSL-RIO2 | 19 | 10 | 0 | 4-20 mA AI | 5069-IF8
684 | RL7-CHR-201-FVI-02 | RL7-CHR-201-FVI-02 |  |  | SERPENTINE ZONE 2A PCW FLOW CONTROL VALVE POSITION FEEDBACK | DG7033 | HX / LA | RL7-INTSL-RIO2 | 19 | 10 | 1 | 4-20 mA AI | 5069-IF8
685 | RL7-CHR-201-FCV-01 | RL7-CHR-201-FCV-01 |  |  | SERPENTINE ZONE 1 PCW CONTROL VALVE | DG7033 | INTSL | RL7-INTSL-RIO2 | 19 | 13 | 0 | 4-20 mA AO | 5069-OF8
686 | RL7-CHR-201-FCV-02 | RL7-CHR-201-FCV-02 |  |  | SERPENTINE ZONE 2 PCW CONTROL VALVE | DG7033 | INTSL | RL7-INTSL-RIO2 | 19 | 13 | 1 | 4-20 mA AO | 5069-OF8
687 | RL7-CNV-205-PB-01 | RL7-CNV-205-PB-01 |  |  | SERPENTINE OUTFEED CONVEYOR E-STOP PULL ROPE SAFETY INPUT CH1 | DG7034 | CHILL | RL7-SERP-RIO1 | 15 | 2 | 2 | 24 VDC SI | 5069-IB8S
688 | RL7-CNV-205-PB-01 | RL7-CNV-205-PB-01 |  |  | SERPENTINE OUTFEED CONVEYOR E-STOP PULL ROPE SAFETY INPUT CH2 | DG7034 | CHILL | RL7-SERP-RIO1 | 15 | 2 | 3 | 24 VDC SI | 5069-IB8S
689 | RL7-CNV-205-ZEC-01 | RL7-CNV-205-ZEC-01 |  |  | DISCHARGE COUNT PE | DG7034 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 8 | 24 VDC DI | 5069-IB16
690 | RL7-CNV-205-ZEC-02 | RL7-CNV-205-ZEC-02 |  |  | DISCHARGE CONVEYOR BLOCKED PE | DG7034 | CHILL | RL7-SERP-RIO1 | 15 | 3 | 11 | 24 VDC DI | 5069-IB16
691 | RL7-CNV-205-XY-01 | RL7-CNV-205-XY-01 |  |  | SERPENTINE DISCHARGE CONVEYOR 1 BACKSTOP RAISE SOLENOID | DG7034 | CHILL | RL7-SERP-RIO1 | 15 | 6 | 1 | 24 VDC DO | 5069-OB16
692 | RL7-CNV-205-XY-02 | RL7-CNV-205-XY-02 |  |  | SERPENTINE DISCHARGE CONVEYOR 1 BACKSTOP LOWER SOLENOID | DG7034 | CHILL | RL7-SERP-RIO1 | 15 | 6 | 2 | 24 VDC DO | 5069-OB16
693 |  | RL7-CNV-401-ZSO-01 |  |  | INSPECTION CONVEYOR REJECT ARM 1 RETRACTED | DG7034 | INTSL | RL7-PKOUT-RIO1 | 17 | 1 | 0 | 24 VDC DI | 5069-OBV8S
694 |  | RL7-CNV-401-ZSC-01 |  |  | INSPECTION CONVEYOR REJECT ARM 1 EXTENDED | DG7034 | INTSL | RL7-PKOUT-RIO1 | 17 | 1 | 1 | 24 VDC DI | 5069-OBV8S
695 |  | RL7-CNV-401-ZSO-02 |  |  | INSPECTION CONVEYOR REJECT ARM 2 RETRACTED | DG7034 | INTSL | RL7-PKOUT-RIO1 | 17 | 1 | 2 | 24 VDC DI | 5069-OBV8S
696 |  | RL7-CNV-401-ZSC-02 |  |  | INSPECTION CONVEYOR REJECT ARM 2 EXTENDED | DG7034 | INTSL | RL7-PKOUT-RIO1 | 17 | 1 | 3 | 24 VDC DI | 5069-OBV8S
697 |  | RL7-CNV-401-PB-01 |  |  | SECONDARY PACKAGING PAUSE BUTTON | DG7034 | INTSL | RL7-PKOUT-RIO1 | 17 | 1 | 8 | 24 VDC DI | 5069-OBV8S
698 |  | RL7-CNV-401-XY-01 |  |  | INSPECTION CONVEYOR REJECT ARMS 1 & 2 SOLENOID VALVE | DG7034 | INTSL | RL7-PKOUT-RIO1 | 17 | 3 | 0 | 24 VDC DO | 5069-OBV8S
699 |  | RL7-CNV-404-ZSO-01 |  |  | CASE PACKER INFEED CONVEYOR 1 REJECT ARM 1 RETRACTED | DG7040 | INTSL | RL7-PKOUT-RIO1 | 17 | 1 | 4 | 24 VDC DI | 5069-OBV8S
700 |  | RL7-CNV-404-ZSC-01 |  |  | CASE PACKER INFEED CONVEYOR 1 REJECT ARM 1 EXTENDED | DG7040 | INTSL | RL7-PKOUT-RIO1 | 17 | 1 | 5 | 24 VDC DI | 5069-OBV8S
701 |  | RL7-CNV-404-ZSO-02 |  |  | CASE PACKER INFEED CONVEYOR 1 REJECT ARM 2 RETRACTED | DG7040 | INTSL | RL7-PKOUT-RIO1 | 17 | 1 | 6 | 24 VDC DI | 5069-OBV8S
702 |  | RL7-CNV-404-ZSC-02 |  |  | CASE PACKER INFEED CONVEYOR 1 REJECT ARM 2 EXTENDED | DG7040 | INTSL | RL7-PKOUT-RIO1 | 17 | 1 | 7 | 24 VDC DI | 5069-OBV8S
703 |  | RL7-CNV-404-XY-01 |  |  | CASE PACKER INFEED CONVEYOR 1 REJECT ARMS 1 & 2 SOLENOID VALVE | DG7040 | INTSL | RL7-PKOUT-RIO1 | 17 | 3 | 1 | 24 VDC DO | 5069-OBV8S
704 | RL7-SKD-201-ZSO-14 | RL7-SKD-201-ZSO-14 |  |  | SERPENTINE CLEAN ASSIST FOAMING HEADER CA SUPPLY OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 0 | 24 VDC DI | 5069-IB16
705 | RL7-SKD-201-ZSC-14 | RL7-SKD-201-ZSC-14 |  |  | SERPENTINE CLEAN ASSIST FOAMING HEADER CA SUPPLY CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 1 | 24 VDC DI | 5069-IB16
706 | RL7-SKD-201-ZSO-02 | RL7-SKD-201-ZSO-02 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 1A OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 2 | 24 VDC DI | 5069-IB16
707 | RL7-SKD-201-ZSC-02 | RL7-SKD-201-ZSC-02 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 1A CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 3 | 24 VDC DI | 5069-IB16
708 | RL7-SKD-201-ZSO-03 | RL7-SKD-201-ZSO-03 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 1B OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 4 | 24 VDC DI | 5069-IB16
709 | RL7-SKD-201-ZSC-03 | RL7-SKD-201-ZSC-03 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 1B CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 5 | 24 VDC DI | 5069-IB16
710 | RL7-SKD-201-ZSO-04 | RL7-SKD-201-ZSO-04 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2A OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 6 | 24 VDC DI | 5069-IB16
711 | RL7-SKD-201-ZSC-04 | RL7-SKD-201-ZSC-04 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2A CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 7 | 24 VDC DI | 5069-IB16
712 | RL7-SKD-201-ZSO-05 | RL7-SKD-201-ZSO-05 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2B OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 8 | 24 VDC DI | 5069-IB16
713 | RL7-SKD-201-ZSC-05 | RL7-SKD-201-ZSC-05 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2B CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 9 | 24 VDC DI | 5069-IB16
714 | RL7-SKD-201-ZSO-06 | RL7-SKD-201-ZSO-06 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2C OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 10 | 24 VDC DI | 5069-IB16
715 | RL7-SKD-201-ZSC-06 | RL7-SKD-201-ZSC-06 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2C CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 11 | 24 VDC DI | 5069-IB16
716 | RL7-SKD-201-ZSO-07 | RL7-SKD-201-ZSO-07 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2D OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 12 | 24 VDC DI | 5069-IB16
717 | RL7-SKD-201-ZSC-07 | RL7-SKD-201-ZSC-07 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2D CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 13 | 24 VDC DI | 5069-IB16
718 | RL7-SKD-201-ZSO-08 | RL7-SKD-201-ZSO-08 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2E OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 14 | 24 VDC DI | 5069-IB16
719 | RL7-SKD-201-ZSC-08 | RL7-SKD-201-ZSC-08 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2E CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 1 | 15 | 24 VDC DI | 5069-IB16
720 | RL7-SKD-201-ZSO-09 | RL7-SKD-201-ZSO-09 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2F OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 0 | 24 VDC DI | 5069-IB16
721 | RL7-SKD-201-ZSC-09 | RL7-SKD-201-ZSC-09 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2F CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 1 | 24 VDC DI | 5069-IB16
722 | RL7-SKD-201-ZSO-10 | RL7-SKD-201-ZSO-10 |  |  | SERPENTINE CLEAN ASSIST PHW END WALLS RINSE OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 2 | 24 VDC DI | 5069-IB16
723 | RL7-SKD-201-ZSC-10 | RL7-SKD-201-ZSC-10 |  |  | SERPENTINE CLEAN ASSIST PHW END WALLS RINSE CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 3 | 24 VDC DI | 5069-IB16
724 | RL7-SKD-201-ZSO-11 | RL7-SKD-201-ZSO-11 |  |  | SERPENTINE CLEAN ASSIST PHW CHAIN RINSE OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 4 | 24 VDC DI | 5069-IB16
725 | RL7-SKD-201-ZSC-11 | RL7-SKD-201-ZSC-11 |  |  | SERPENTINE CLEAN ASSIST PHW CHAIN RINSE CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 5 | 24 VDC DI | 5069-IB16
726 | RL7-SKD-201-ZSO-12 | RL7-SKD-201-ZSO-12 |  |  | SERPENTINE CLEAN ASSIST FOAMING HEADER PCW SUPPLY OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 6 | 24 VDC DI | 5069-IB16
727 | RL7-SKD-201-ZSC-12 | RL7-SKD-201-ZSC-12 |  |  | SERPENTINE CLEAN ASSIST FOAMING HEADER PCW SUPPLY CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 7 | 24 VDC DI | 5069-IB16
728 | RL7-SKD-201-ZSO-13 | RL7-SKD-201-ZSO-13 |  |  | SERPENTINE CLEAN ASSIST FOAMING HEADER FOAM SUPPLY OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 8 | 24 VDC DI | 5069-IB16
729 | RL7-SKD-201-ZSC-13 | RL7-SKD-201-ZSC-13 |  |  | SERPENTINE CLEAN ASSIST FOAMING HEADER FOAM SUPPLY CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 9 | 24 VDC DI | 5069-IB16
730 | RL7-SKD-201-ZSO-15 | RL7-SKD-201-ZSO-15 |  |  | SERPENTINE CLEAN ASSIST PCW BASIN RINSE VALVE OPEN LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 10 | 24 VDC DI | 5069-IB16
731 | RL7-SKD-201-ZSC-15 | RL7-SKD-201-ZSC-15 |  |  | SERPENTINE CLEAN ASSIST PCW BASIN RINSE VALVE CLOSED LIMIT SWITCH | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 2 | 11 | 24 VDC DI | 5069-IB16
732 | RL7-SKD-201-XY-05 | RL7-SKD-201-XY-05 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2B VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 0 | 24 VDC DO | 5069-OB16
733 | RL7-SKD-201-XY-06 | RL7-SKD-201-XY-06 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2C VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 1 | 24 VDC DO | 5069-OB16
734 | RL7-SKD-201-XY-07 | RL7-SKD-201-XY-07 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2D VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 2 | 24 VDC DO | 5069-OB16
735 | RL7-SKD-201-XY-08 | RL7-SKD-201-XY-08 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2E VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 3 | 24 VDC DO | 5069-OB16
736 | RL7-SKD-201-XY-09 | RL7-SKD-201-XY-09 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2F VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 4 | 24 VDC DO | 5069-OB16
737 | RL7-SKD-201-XY-10 | RL7-SKD-201-XY-10 |  |  | SERPENTINE CLEAN ASSIST PHW END WALLS RINSE VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 5 | 24 VDC DO | 5069-OB16
738 | RL7-SKD-201-XY-11 | RL7-SKD-201-XY-11 |  |  | SERPENTINE CLEAN ASSIST PHW CHAIN RINSE VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 6 | 24 VDC DO | 5069-OB16
739 | RL7-SKD-201-XV-02 | RL7-SKD-201-XV-02 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 1A VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 7 | 24 VDC DO | 5069-OB16
740 | RL7-SKD-201-XY-03 | RL7-SKD-201-XY-03 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 1B VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 8 | 24 VDC DO | 5069-OB16
741 | RL7-SKD-201-XY-04 | RL7-SKD-201-XY-04 |  |  | SERPENTINE CLEAN ASSIST PHW PAN RINSE ZONE 2A VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 9 | 24 VDC DO | 5069-OB16
742 | RL7-SKD-201-XV-12 | RL7-SKD-201-XV-12 |  |  | SERPENTINE CLEAN ASSIST FOAMING HEADER PCW SUPPLY VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 10 | 24 VDC DO | 5069-OB16
743 | RL7-SKD-201-XV-13 | RL7-SKD-201-XV-13 |  |  | SERPENTINE CLEAN ASSIST FOAMING HEADER FOAM SUPPLY VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 11 | 24 VDC DO | 5069-OB16
744 | RL7-SKD-201-XV-14 | RL7-SKD-201-XV-14 |  |  | SERPENTINE CLEAN ASSIST FOAMING HEADER CA SUPPLY VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 12 | 24 VDC DO | 5069-OB16
745 | RL7-SKD-201-XV-15 | RL7-SKD-201-XV-15 |  |  | SERPENTINE CLEAN ASSIST PCW BASIN RINSE VALVE OPEN SOLENOID | DG7602 | INTSL | RL7-INTSL-RIO2 | 19 | 5 | 13 | 24 VDC DO | 5069-OB16
746 | RL7-SKD-102-PIT-02 | RL7-SKD-102-PIT-02 |  |  | LACTIC ACID SKID PUMP DISCHARGE PRESSURE | DG7604 | HX / LA | RL7-INTSL-RIO2 | 19 | 10 | 2 | 4-20 mA AI | 5069-IF8
747 | RL7-CKR-101-ZSO-27 | RL7-CKR-101-ZSO-27 |  |  | COOKER 1 JHWS BLOCK VALVE OPEN LIMIT SWITCH | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 1 | 2 | 24 VDC DI | 5069-IB16
748 | RL7-CKR-101-ZSC-27 | RL7-CKR-101-ZSC-27 |  |  | COOKER 1 JHWS BLOCK VALVE CLOSED LIMIT SWITCH | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 1 | 3 | 24 VDC DI | 5069-IB16
749 | RL7-CKR-102-ZSO-27 | RL7-CKR-102-ZSO-27 |  |  | COOKER 2 JHWS BLOCK VALVE OPEN LIMIT SWITCH | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 2 | 2 | 24 VDC DI | 5069-IB16
750 | RL7-CKR-102-ZSC-27 | RL7-CKR-102-ZSC-27 |  |  | COOKER 2 JHWS BLOCK VALVE CLOSED LIMIT SWITCH | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 2 | 3 | 24 VDC DI | 5069-IB16
751 | RL7-AGC-201-ZSO-27 | RL7-AGC-201-ZSO-27 |  |  | DISCHARGE AUGER CART JHWS BLOCK VALVE OPEN LIMIT SWITCH | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 2 | 8 | 24 VDC DI | 5069-IB16
752 | RL7-AGC-201-ZSC-27 | RL7-AGC-201-ZSC-27 |  |  | DISCHARGE AUGER CART JHWS BLOCK VALVE CLOSED LIMIT SWITCH | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 2 | 9 | 24 VDC DI | 5069-IB16
753 | RL7-CKR-102-XV-27 | RL7-CKR-102-XV-27 |  |  | COOKER 2 JHWS BLOCK VALVE OPEN SOLENOID | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 4 | 0 | 24 VDC DO | 5069-OB16
754 | RL7-AGC-101-XV-27 | RL7-AGC-201-XV-27 |  |  | DISCHARGE AUGER CART JHWS BLOCK VALVE OPEN SOLENOID | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 4 | 4 | 24 VDC DO | 5069-OB16
755 | RL7-CKR-101-TIT-03 | RL7-CKR-101-TIT-03 |  |  | COOKER 1 JHWR TEMPERATURE | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 6 | 5 | 4-20 mA AI | 5069-IF8 | 0 - 130 LB/MIN
756 | RL7-CKR-102-TIT-03 | RL7-CKR-102-TIT-03 |  |  | COOKER 2 JHWR TEMPERATURE | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 7 | 5 | 4-20 mA AI | 5069-IF8 | 0 - 300 F
757 | RL7-AGC-201-TIT-03 | RL7-AGC-201-TIT-03 |  |  | DISCHARGE AUGER CART JHWR TEMPERATURE | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 8 | 1 | 4-20 mA AI | 5069-IF8 | 0 - 150 PSI
758 | RL7-CKR-101-FIT-01 | RL7-CKR-101-FIT-01 |  |  | COOKER 1 JHWS FLOW | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 9 | 0 | 4-20 mA AI | 5069-IF8 | 0 - 100%
759 | RL7-CKR-101-TVI-01 | RL7-CKR-101-TVI-01 |  |  | COOKER 1 JHWR CONTROL VALVE POSITION FEEDBACK | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 9 | 1 | 4-20 mA AI | 5069-IF8
760 | RL7-CKR-102-FIT-01 | RL7-CKR-102-FIT-01 |  |  | COOKER 2 JHWS FLOW | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 10 | 0 | 4-20 mA AI | 5069-IF8
761 | RL7-CKR-102-TVI-01 | RL7-CKR-102-TVI-01 |  |  | COOKER 2 JHWR CONTROL VALVE POSITION FEEDBACK | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 10 | 1 | 4-20 mA AI | 5069-IF8
762 | RL7-AGC-201-FIT-01 | RL7-AGC-201-FIT-01 |  |  | DISCHARGE AUGER CART JHWS FLOW | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 10 | 3 | 4-20 mA AI | 5069-IF8
763 | RL7-AGC-201-TVI-01 | RL7-AGC-201-TVI-01 |  |  | DISCHARGE AUGER CART JHWR CONTROL VALVE POSITION FEEBACK | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 10 | 4 | 4-20 mA AI | 5069-IF8
764 | RL7-CKR-101-TCV-01 | RL7-CKR-101-TCV-01 |  |  | COOKER 1 JHWR CONTROL VALVE | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 12 | 1 | 4-20 mA AO | 5069-OF8
765 | RL7-CKR-102-TCV-101 | RL7-CKR-102-TCV-101 |  |  | COOKER 2 HPS CONTROL VALVE | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 13 | 0 | 4-20 mA AO | 5069-OF8
766 | RL7-AGC-201-TCV-01 | RL7-AGC-201-TCV-01 |  |  | DISCHARGE AUGER CART JHWR CONTROL VALVE | DG7606 | INTSL | RL7-INTSL-RIO1 | 18 | 13 | 3 | 4-20 mA AO | 5069-OF8
767 | RL7-TNK-102-XV-01-ZSO | RL7-TNK-102-ZSO-01 |  |  | DXP WATER INLET VALVE OPEN LIMIT SWITCH | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 0 | 0 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
768 | RL7-TNK-102-XV-01-ZSC | RL7-TNK-102-ZSC-01 |  |  | DXP WATER INLET VALVE CLOSED LIMIT SWITCH | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 0 | 1 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
769 | RL7-TNK-102-ZSO-02 | RL7-TNK-102-ZSO-02 |  |  | DXP SYSTEM BYPASS VALVE OPEN LIMIT SWITCH | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 0 | 2 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
770 | RL7-TNK-102-ZSC-02 | RL7-TNK-102-ZSC-02 |  |  | DXP SYSTEM BYPASS VALVE CLOSED LIMIT SWITCH | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 0 | 3 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
771 | RL7-HTX-101-XV-01-ZSO | RL7-HTX-101-XV-01-ZSO |  |  | DXP HEX IN VALVE OPEN LIMIT SWITCH | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 0 | 4 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
772 | RL7-HTX-101-XV-01-ZSC | RL7-HTX-101-XV-01-ZSC |  |  | DXP HEX IN VALVE CLOSED LIMIT SWITCH | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 0 | 5 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
773 | RL7-TNK-102-XV-01 | RL7-TNK-102-XV-01 |  |  | DXP WATER INLET VALVE OPEN SOLENOID | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 1 | 0 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
774 | RL7-TNK-102-XV-02 | RL7-TNK-102-XV-02 |  |  | DXP SYSTEM BYPASSS VALVE OPEN SOLENOID | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 1 | 1 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
775 | RL7-HTX-101-XV-01 | RL7-HTX-101-XV-01 |  |  | DXP HEX IN VALVE OPEN SOLENOID | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 1 | 2 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
776 | RL7-TNK-102-FIT-01 | RL7-TNK-102-FIT-01 |  |  | DXP WATER INLET FLOW TRANSMITTER | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 2 | 0 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
777 | RL7-HTX-101-FIT-01 | RL7-HTX-101-FIT-01 |  |  | DXP HEX FLOW IN TRANSMITTER | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 2 | 1 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
778 | RL7-TNK-102-LIT-01 | RL7-TNK-102-LIT-01 |  |  | DXP TANK LEVEL TRANSMITTER | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 2 | 2 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
779 | RL7-PMP-108-PIT-01 | RL7-PMP-108-PIT-01 |  |  | DXP SYSTEM PRESSURE IN TRANSMITTER | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 2 | 3 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
780 | RL7-TNK-102-PIT-01 | RL7-TNK-102-PIT-01 |  |  | DXP WATER INLET PRESSURE TRANSMITTER | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 2 | 4 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
781 | RL7-HTX-101-PIT-01 | RL7-HTX-101-PIT-01 |  |  | DXP HEX PRESSURE IN TRANSMITTER | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 2 | 5 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
782 | RL7-HTX-101-TVI-01 | RL7-HTX-101-TVI-01 |  |  | DXP TEMPERATURE CONTROL VALVE POSITION FEEDBACK | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 2 | 6 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
783 | RL7-TNK-102-TT-01 | RL7-TNK-102-TT-01 |  |  | DXP TANK TEMPERATURE TRANSMITTER | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 2 | 7 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
784 | RL7-HTX-101-TT-01 | RL7-HTX-101-TT-01 |  |  | DXP SUPPLY TEMPERATURE | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 3 | 0 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
785 | RL7-HTX-101-TCV-01 | RL7-HTX-101-TCV-01 |  |  | DXP HOT WATER TCV | DG7606 | HX / LA | RL7-DXPHX-RIO1 | 20 | 4 | 0 | 4-20 mA AO | 5069-OF8 | [11 empty] | OEM PANEL
786 | RL7-CKR-101-ZSO-101 | RL7-CKR-101-ZSO-101 |  |  | COOKER 1 HPS BLOCK VALVE OPEN LIMIT SWITCH | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 1 | 4 | 24 VDC DI | 5069-IB16
787 | RL7-CKR-101-ZSC-101 | RL7-CKR-101-ZSC-101 |  |  | COOKER 1 HPS BLOCK VALVE CLOSED LIMIT SWITCH | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 1 | 5 | 24 VDC DI | 5069-IB16
788 | RL7-CKR-102-ZSO-101 | RL7-CKR-102-ZSO-101 |  |  | COOKER 2 HPS BLOCK VALVE OPEN LIMIT SWITCH | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 2 | 4 | 24 VDC DI | 5069-IB16
789 | RL7-CKR-102-ZSC-101 | RL7-CKR-102-ZSC-101 |  |  | COOKER 2 HPS BLOCK VALVE CLOSED LIMIT SWITCH | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 2 | 5 | 24 VDC DI | 5069-IB16
790 | RL7-CKR-101-XV-101 | RL7-CKR-101-XV-101 |  |  | COOKER 1 HPS BLOCK VALVE OPEN SOLENOID | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 3 | 1 | 24 VDC DO | 5069-OB16
791 | RL7-CKR-102-XV-101 | RL7-CKR-102-XV-101 |  |  | COOKER 2 HPS BLOCK VALVE OPEN SOLENOID | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 4 | 1 | 24 VDC DO | 5069-OB16
792 | RL7-CKR-101-FIT-101 | RL7-CKR-101-FIT-101 |  |  | COOKER 1 HPS FLOW | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 6 | 0 | 4-20 mA AI | 5069-IF8 | 0 - 7000 LB/HR
793 | RL7-CKR-101-PIT-101 | RL7-CKR-101-PIT-101 |  |  | COOKER 1 HPS BYPASS PRESSURE | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 6 | 1 | 4-20 mA AI | 5069-IF8 | 0 - 10 BAR
794 | RL7-CKR-101-PIT-102 | RL7-CKR-101-PIT-102 |  |  | COOKER 1 HPS PRESSURE | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 6 | 2 | 4-20 mA AI | 5069-IF8 | 0 - 10 BAR
795 | RL7-CKR-101-TVI-101 | RL7-CKR-101-TVI-101 |  |  | COOKER 1 HPS CONTROL VALVE POSITION FEEDBACK | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 6 | 3 | 4-20 mA AI | 5069-IF8 | [11 empty] | RL7-HTX-101A-TT-02
796 | RL7-CKR-102-FIT-101 | RL7-CKR-102-FIT-101 |  |  | COOKER 2 HPS FLOW | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 7 | 0 | 4-20 mA AI | 5069-IF8 | 0 - 7000 LB/HR
797 | RL7-CKR-102-PIT-101 | RL7-CKR-102-PIT-101 |  |  | COOKER 2 HPS BYPASS PRESSURE | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 7 | 1 | 4-20 mA AI | 5069-IF8 | 0 - 10 BAR
798 | RL7-CKR-102-PIT-102 | RL7-CKR-102-PIT-102 |  |  | COOKER 2 HPS PRESSURE | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 7 | 2 | 4-20 mA AI | 5069-IF8 | 0 - 10 BAR
799 | RL7-CKR-102-TVI-101 | RL7-CKR-102-TVI-101 |  |  | COOKER 2 HPS CONTROL VALVE POSITION FEEDBACK | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 7 | 3 | 4-20 mA AI | 5069-IF8 | [11 empty] | RL7-HTX-101B-TT-02
800 |  | RL7-CKR-200-PIT-101 |  |  | PHASE 2A COOKERS HPS HEADER PRESSURE | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 8 | 3 | 4-20 mA AI | 5069-IF8
801 | RL7-CKR-101-TCV-101 | RL7-CKR-101-TCV-101 |  |  | COOKER 1 HPS CONTROL VALVE | DG7700 | INTSL | RL7-INTSL-RIO1 | 18 | 12 | 0 | 4-20 mA AO | 5069-OF8
802 | RL7-CKR-103-PIT-101 | RL7-CKR-103-PIT-101 |  |  | HOT WATER JACKET SYSTEM HPS PRESSURE | DG7701 | INTSL | RL7-INTSL-RIO1 | 18 | 8 | 0 | 4-20 mA AI | 5069-IF8 | 0 - 10 BAR | [10 empty] | RL7-HTX-101A-LT-01
803 | RL7-CKR-101-XV-27 | RL7-CKR-101-XV-27 |  |  | COOKER 1 JHWS BLOCK VALVE OPEN SOLENOID | DG7702 | INTSL | RL7-INTSL-RIO1 | 18 | 3 | 0 | 24 VDC DO | 5069-OB16
804 | RL7-CKR-102-TCV-01 | RL7-CKR-102-TCV-01 |  |  | COOKER 2 JHWR CONTROL VALVE | DG7702 | INTSL | RL7-INTSL-RIO1 | 18 | 13 | 1 | 4-20 mA AO | 5069-OF8
805 | RL7-HTX-ABC-YS-01 | RL7-HTX-ABC-YS-01 |  |  | CHILLERS A,B, & C VALVE CONTROL POWER STATUS OK | N/A | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 9 | 24 VDC DI | 5069-IB16
806 | RL7-HTX-201A-LS-01 | RL7-HTX-201A-LS-01 |  |  | SHELL & TUBE CHILLER A NH3 LOW LEVEL SWITCH | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 8 | 24 VDC DI | 5069-IB16
807 | RL7-HTX-201A-LS-02 | RL7-HTX-201A-LS-02 |  |  | SHELL & TUBE CHILLER A BACKUP OPERATING NH3 LEVEL SWITCH | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 3 | 10 | 24 VDC DI | 5069-IB16
808 | RL7-HTX-101A-YS-01 | RL7-HTX-101A-YS-01 |  |  | SHELL & TUBE CHILLER A COOLANT SUPPLY VALVE OPEN SOLENOID | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 6 | 0 | 24 VDC DO | 5069-OB16
809 | RL7-HTX-101A-YS-02 | RL7-HTX-101A-YS-02 |  |  | SHELL & TUBE CHILLER A COOLANT RETURN VALVE OPEN SOLENOID | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 6 | 1 | 24 VDC DO | 5069-OB16
810 | RL7-HTX-101A-YS-03 | RL7-HTX-101A-YS-03 |  |  | SHELL & TUBE CHILLER A HOT GAS SUPPLY VALVE OPEN SOLENOID | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 6 | 2 | 24 VDC DO | 5069-OB16
811 | RL7-HTX-101A-YS-04 | RL7-HTX-101A-YS-04 |  |  | SHELL & TUBE CHILLER A PUMP OUT SUPPLY VALVE OPEN SOLENOID | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 6 | 3 | 24 VDC DO | 5069-OB16
812 | RL7-HTX-101B-YS-01 | RL7-HTX-101B-YS-01 |  |  | FALLING FILM CHILLER B COOLANT SUPPLY VALVE OPEN SOLENOID | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 6 | 4 | 24 VDC DO | 5069-OB16
813 | RL7-HTX-101B-YS-02 | RL7-HTX-101B-YS-02 |  |  | FALLING FILM CHILLER B COOLANT RETURN VALVE OPEN SOLENOID | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 6 | 5 | 24 VDC DO | 5069-OB16
814 | RL7-HTX-101C-YS-01 | RL7-HTX-101C-YS-01 |  |  | FALLING FILM CHILLER C COOLANT SUPPLY VALVE OPEN SOLENOID | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 6 | 6 | 24 VDC DO | 5069-OB16
815 | RL7-HTX-101C-YS-02 | RL7-HTX-101C-YS-02 |  |  | FALLING FILM CHILLER C COOLANT RETURN VALVE OPEN SOLENOID | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 6 | 7 | 24 VDC DO | 5069-OB16
816 | RL7-HTX-101A-LT-01 | RL7-HTX-101A-LT-01 |  |  | SHELL & TUBE CHILLER A NH3 LEVEL | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 9 | 0 | 4-20 mA AI | 5069-IF8 | [11 empty] | RL7-HTX-101A-LT-01
817 | RL7-HTX-101A-TIT-02 | RL7-HTX-101A-TIT-02 |  |  | SHELL & TUBE CHILLER A OUTLET TEMPERATURE | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 9 | 1 | 4-20 mA AI | 5069-IF8 | [11 empty] | RL7-HTX-101A-TT-02
818 | RL7-HTX-101B-TIT-02 | RL7-HTX-101B-TIT-02 |  |  | FALLING FILM CHILLER B OUTLET TEMPERATURE | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 9 | 2 | 4-20 mA AI | 5069-IF8 | [11 empty] | RL7-HTX-101B-TT-02
819 | RL7-HTX-101C-TIT-02 | RL7-HTX-101C-TIT-02 |  |  | FALLING FILM CHILLER C OUTLET TEMPERATURE | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 9 | 3 | 4-20 mA AI | 5069-IF8 | [11 empty] | RL7-HTX-101C-TT-02
820 | RL7-HTX-101A-TIT-01 | RL7-HTX-101A-TIT-01 |  |  | SHELL & TUBE CHILLER A INLET TEMPERATURE | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 9 | 4 | 4-20 mA AI | 5069-IF8 | (-50 to 150 C) | [10 empty] | RL7-HTX-101A-TT-01
821 | RL7-HTX-101B-TIT-01 | RL7-HTX-101B-TIT-01 |  |  | FALLING FILM CHILLER B INLET TEMPERATURE | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 9 | 5 | 4-20 mA AI | 5069-IF8 | (-50 to 150 C) | [10 empty] | RL7-HTX-101B-TT-01
822 | RL7-HTX-101C-TIT-01 | RL7-HTX-101C-TIT-01 |  |  | FALLING FILM CHILLER C INLET TEMPERATURE | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 9 | 6 | 4-20 mA AI | 5069-IF8 | (-50 to 150 C) | [10 empty] | RL7-HTX-101C-TT-02
823 | RL7-HTX-101A-CV-01E | RL7-HTX-101A-CV-01E |  |  | SHELL & TUBE CHILLER A COOLANT SUPPLY MOTOR OPERATED VALVE | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 13 | 2 | 4-20 mA AO | 5069-OF8
824 | RL7-HTX-201A-CVI-01E | RL7-HTX-201A-CVI-01E |  |  | SHELL & TUBE CHILLER A COOLANT SUPPLY MOV POSITION FEEDBACK | R7011 | INTSL | RL7-INTSL-RIO2 | 19 | 14 | 0 | I/V/T AI | 5069-IY4
[9 empty] | 0 | 0 | 0
825 | RL7-CNV-109-ZSS-10 |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 4 | 2 | 24 VDC SI | 5069-IB8S
826 | RL7-CNV-109-ZSS-10 |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 4 | 3 | 24 VDC SI | 5069-IB8S
827 | RL7-CNV-109-PB-01 |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 4 | 4 | 24 VDC SI | 5069-IB8S
828 | RL7-CNV-109-PB-01 |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 4 | 5 | 24 VDC SI | 5069-IB8S
829 | RL7-GRR-103-ZSS-05 |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 5 | 0 | 24 VDC SI | 5069-IB8S
830 | RL7-GRR-103-ZSS-05 |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 5 | 1 | 24 VDC SI | 5069-IB8S
831 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 5 | 2 | 24 VDC SI | 5069-IB8S
832 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 5 | 3 | 24 VDC SI | 5069-IB8S
833 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 5 | 4 | 24 VDC SI | 5069-IB8S
834 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 5 | 5 | 24 VDC SI | 5069-IB8S
835 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 5 | 6 | 24 VDC SI | 5069-IB8S
836 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 5 | 7 | 24 VDC SI | 5069-IB8S
837 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 1 | 24 VDC DI | 5069-IB16
838 | RL7-GRR-103-PSL-01 |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 2 | 24 VDC DI | 5069-IB16
839 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 3 | 24 VDC DI | 5069-IB16
840 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 4 | 24 VDC DI | 5069-IB16
841 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 5 | 24 VDC DI | 5069-IB16
842 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 6 | 24 VDC DI | 5069-IB16
843 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 7 | 24 VDC DI | 5069-IB16
844 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 8 | 24 VDC DI | 5069-IB16
845 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 9 | 24 VDC DI | 5069-IB16
846 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 10 | 24 VDC DI | 5069-IB16
847 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 11 | 24 VDC DI | 5069-IB16
848 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 12 | 24 VDC DI | 5069-IB16
849 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 13 | 24 VDC DI | 5069-IB16
850 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 14 | 24 VDC DI | 5069-IB16
851 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 6 | 15 | 24 VDC DI | 5069-IB16
852 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-PBK-RIO1 | 1 | 7 | 0 | ARM | 5069-ARM
853 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 8 | 0 | 24 VDC DO | 5069-OB16
854 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 8 | 8 | 24 VDC DO | 5069-OB16
855 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 8 | 9 | 24 VDC DO | 5069-OB16
856 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 8 | 10 | 24 VDC DO | 5069-OB16
857 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 8 | 12 | 24 VDC DO | 5069-OB16
858 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 8 | 13 | 24 VDC DO | 5069-OB16
859 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 8 | 14 | 24 VDC DO | 5069-OB16
860 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 0 | 24 VDC DO | 5069-OB16
861 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 2 | 24 VDC DO | 5069-OB16
862 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 3 | 24 VDC DO | 5069-OB16
863 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 4 | 24 VDC DO | 5069-OB16
864 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 5 | 24 VDC DO | 5069-OB16
865 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 6 | 24 VDC DO | 5069-OB16
866 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 7 | 24 VDC DO | 5069-OB16
867 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 8 | 24 VDC DO | 5069-OB16
868 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 9 | 24 VDC DO | 5069-OB16
869 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 10 | 24 VDC DO | 5069-OB16
870 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 11 | 24 VDC DO | 5069-OB16
871 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 12 | 24 VDC DO | 5069-OB16
872 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 13 | 24 VDC DO | 5069-OB16
873 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 14 | 24 VDC DO | 5069-OB16
874 |  |  |  |  | SPARE |  |  | RL7-PBK-RIO1 | 1 | 9 | 15 | 24 VDC DO | 5069-OB16
875 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 2 | 8 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
876 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 2 | 9 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
877 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 2 | 10 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
878 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 2 | 11 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
879 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 2 | 12 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
880 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 2 | 13 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
881 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 2 | 14 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
882 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 2 | 15 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
883 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 3 | 15 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
884 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 0 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
885 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 1 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
886 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 2 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
887 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 3 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
888 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 4 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
889 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 5 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
890 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 6 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
891 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 7 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
892 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 8 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
893 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 9 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
894 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 10 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
895 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 11 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
896 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 12 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
897 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 13 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
898 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 14 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
899 |  |  |  |  | SPARE |  |  | RL7-LFT-RIO1 | 2 | 4 | 15 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
899 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 1 | 0 | 24 VDC SI | 5069-IB8S
901 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 1 | 1 | 24 VDC SI | 5069-IB8S
902 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 1 | 2 | 24 VDC SI | 5069-IB8S
903 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 1 | 3 | 24 VDC SI | 5069-IB8S
904 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 1 | 4 | 24 VDC SI | 5069-IB8S
905 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 1 | 5 | 24 VDC SI | 5069-IB8S
906 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 1 | 6 | 24 VDC SI | 5069-IB8S
907 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 1 | 7 | 24 VDC SI | 5069-IB8S
908 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-BINS-RIO1 | 3 | 2 | 0 | ARM | 5069-ARM
909 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 3 | 10 | 24 VDC DI | 5069-IB8S
910 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 3 | 11 | 24 VDC DI | 5069-IB8S
911 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 3 | 12 | 24 VDC DI | 5069-IB8S
912 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 3 | 13 | 24 VDC DI | 5069-IB8S
913 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 3 | 14 | 24 VDC DI | 5069-IB8S
914 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 3 | 15 | 24 VDC DI | 5069-IB8S
915 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 4 | 12 | 24 VDC DO | 5069-IB16
916 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 4 | 13 | 24 VDC DO | 5069-IB16
917 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 4 | 14 | 24 VDC DO | 5069-IB16
918 |  |  |  |  | SPARE |  |  | RL7-BINS-RIO1 | 3 | 4 | 15 | 24 VDC DO | 5069-IB16
919 | RL7-BIN-102-ZSS-03 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 2 | 6 | 24 VDC SI | 5069-IB8S
920 | RL7-BIN-102-ZSS-03 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 2 | 7 | 24 VDC SI | 5069-IB8S
921 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 3 | 0 | 24 VDC SI | 5069-IB8S
922 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 3 | 1 | 24 VDC SI | 5069-IB8S
923 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 3 | 2 | 24 VDC SI | 5069-IB8S
924 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 3 | 3 | 24 VDC SI | 5069-IB8S
925 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 3 | 4 | 24 VDC SI | 5069-IB8S
926 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 3 | 5 | 24 VDC SI | 5069-IB8S
927 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 3 | 6 | 24 VDC SI | 5069-IB8S
928 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 3 | 7 | 24 VDC SI | 5069-IB8S
929 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-BINA-RIO1 | 4 | 4 | 0 | ARM | 5069-ARM
930 | RL7-CNV-111-ZSO-01 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 0 | 24 VDC DI | 5069-IB16
931 | RL7-CNV-111-ZSC-01 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 1 | 24 VDC DI | 5069-IB16
932 | RL7-CNV-111-ZSO-02 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 2 | 24 VDC DI | 5069-IB16
933 | RL7-CNV-111-ZSC-02 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 3 | 24 VDC DI | 5069-IB16
934 | RL7-CNV-111-ZSO-03 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 4 | 24 VDC DI | 5069-IB16
935 | RL7-CNV-111-ZSC-03 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 5 | 24 VDC DI | 5069-IB16
936 | RL7-CNV-111-ZSO-04 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 6 | 24 VDC DI | 5069-IB16
937 | RL7-CNV-111-ZSC-04 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 7 | 24 VDC DI | 5069-IB16
938 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 8 | 24 VDC DI | 5069-IB16
939 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 9 | 24 VDC DI | 5069-IB16
940 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 10 | 24 VDC DI | 5069-IB16
941 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 11 | 24 VDC DI | 5069-IB16
942 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 12 | 24 VDC DI | 5069-IB16
943 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 13 | 24 VDC DI | 5069-IB16
944 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 14 | 24 VDC DI | 5069-IB16
945 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 5 | 15 | 24 VDC DI | 5069-IB16
946 | RL7-CNV-111-ZSC-05 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 6 | 7 | 24 VDC DO | 5069-IB16
947 | RL7-BIN-101-ZSO-01 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 6 | 8 | 24 VDC DO | 5069-IB16
948 | RL7-BIN-101-ZSC-01 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 6 | 9 | 24 VDC DO | 5069-IB16
949 | RL7-BIN-102-ZSO-01 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 6 | 10 | 24 VDC DO | 5069-IB16
950 | RL7-BIN-102-ZSC-01 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 6 | 11 | 24 VDC DO | 5069-IB16
951 | RL7-CNV-112-ZSO-01 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 6 | 12 | 24 VDC DO | 5069-IB16
952 | RL7-CNV-112-ZSC-01 |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 6 | 13 | 24 VDC DO | 5069-IB16
953 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 6 | 14 | 24 VDC DO | 5069-IB16
954 |  |  |  |  | SPARE |  |  | RL7-BINA-RIO1 | 4 | 6 | 15 | 24 VDC DO | 5069-IB16
955 | RL7-CNV-114-ZSS-04 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 3 | 0 | 24 VDC SI | 5069-IB8S
956 | RL7-CNV-114-ZSS-04 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 3 | 1 | 24 VDC SI | 5069-IB8S
957 | RL7-CNV-114-ZSS-01 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 3 | 2 | 24 VDC SI | 5069-IB8S
958 | RL7-CNV-114-ZSS-01 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 3 | 3 | 24 VDC SI | 5069-IB8S
959 | RL7-CNV-114-ZSS-02 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 3 | 4 | 24 VDC SI | 5069-IB8S
960 | RL7-CNV-114-ZSS-02 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 3 | 5 | 24 VDC SI | 5069-IB8S
961 | RL7-CNV-114-ZSS-03 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 3 | 6 | 24 VDC SI | 5069-IB8S
962 | RL7-CNV-114-ZSS-03 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 3 | 7 | 24 VDC SI | 5069-IB8S
963 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-BINB-RIO1 | 5 | 4 | 0 | ARM | 5069-ARM
964 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 0 | 24 VDC DI | 5069-IB8S
965 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 1 | 24 VDC DI | 5069-IB8S
966 | RL7-CNV-113-ZSS-01 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 2 | 24 VDC DI | 5069-IB8S
967 | RL7-CNV-113-ZSS-01 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 3 | 24 VDC DI | 5069-IB8S
968 | RL7-CNV-112-PB-01 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 4 | 24 VDC DI | 5069-IB8S
969 | RL7-CNV-112-PB-01 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 5 | 24 VDC DI | 5069-IB8S
970 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 6 | 24 VDC DI | 5069-IB8S
971 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 7 | 24 VDC DI | 5069-IB8S
972 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 8 | 24 VDC DI | 5069-IB16
973 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 9 | 24 VDC DI | 5069-IB16
974 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 10 | 24 VDC DI | 5069-IB16
975 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 11 | 24 VDC DI | 5069-IB16
976 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 12 | 24 VDC DI | 5069-IB16
977 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 13 | 24 VDC DI | 5069-IB16
978 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 14 | 24 VDC DI | 5069-IB16
979 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 5 | 15 | 24 VDC DI | 5069-IB16
980 | RL7-BIN-104-ZSO-01 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 6 | 9 | 24 VDC DO | 5069-IB16
981 | RL7-BIN-104-ZSC-01 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 6 | 10 | 24 VDC DO | 5069-IB16
982 | RL7-CNV-113-ZSO-01 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 6 | 11 | 24 VDC DO | 5069-IB16
983 | RL7-CNV-113-ZSC-01 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 6 | 12 | 24 VDC DO | 5069-IB16
984 | RL7-CNV-114-ZSO-08 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 6 | 13 | 24 VDC DO | 5069-IB16
985 | RL7-CNV-114-ZSC-08 |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 6 | 14 | 24 VDC DO | 5069-IB16
986 |  |  |  |  | SPARE |  |  | RL7-BINB-RIO1 | 5 | 6 | 15 | 24 VDC DO | 5069-IB16
988 | RL7-CNV-114-ZSS-05 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 2 | 4 | 24 VDC SI | 5069-IB8S
989 | RL7-CNV-114-ZSS-05 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 2 | 5 | 24 VDC SI | 5069-IB8S
990 | RL7-BIN-104-ZSS-03 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 2 | 6 | 24 VDC SI | 5069-IB8S
991 | RL7-BIN-104-ZSS-03 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 2 | 7 | 24 VDC SI | 5069-IB8S
992 | RL7-CNV-114-ZSS-04 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 3 | 0 | 24 VDC SI | 5069-IB8S
993 | RL7-CNV-114-ZSS-04 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 3 | 1 | 24 VDC SI | 5069-IB8S
994 | RL7-CNV-114-ZSS-01 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 3 | 2 | 24 VDC SI | 5069-IB8S
995 | RL7-CNV-114-ZSS-01 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 3 | 3 | 24 VDC SI | 5069-IB8S
996 | RL7-CNV-114-ZSS-02 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 3 | 4 | 24 VDC SI | 5069-IB8S
997 | RL7-CNV-114-ZSS-02 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 3 | 5 | 24 VDC SI | 5069-IB8S
998 | RL7-CNV-114-ZSS-03 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 3 | 6 | 24 VDC SI | 5069-IB8S
999 | RL7-CNV-114-ZSS-03 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 3 | 7 | 24 VDC SI | 5069-IB8S
1000 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 4 | 6 | 24 VDC DI | 5069-IB8S
1001 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 4 | 7 | 24 VDC DI | 5069-IB8S
1002 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 4 | 8 | 24 VDC DI | 5069-IB16
1003 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 4 | 9 | 24 VDC DI | 5069-IB16
1004 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 4 | 10 | 24 VDC DI | 5069-IB16
1005 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 4 | 11 | 24 VDC DI | 5069-IB16
1006 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 4 | 12 | 24 VDC DI | 5069-IB16
1007 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 4 | 13 | 24 VDC DI | 5069-IB16
1008 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 4 | 14 | 24 VDC DI | 5069-IB16
1009 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 4 | 15 | 24 VDC DI | 5069-IB16
1010 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-IPA1-RIO1 | 6 | 5 | 0 | ARM | 5069-ARM
1011 | RL7-CNV-114-ZSC-04 | [6 empty] | RL7-IPA1-RIO1 | 6 | 6 | 4 | 24 VDC DO | 5069-IB16
1012 | RL7-CNV-114-ZSC-03 | [6 empty] | RL7-IPA1-RIO1 | 6 | 6 | 5 | 24 VDC DO | 5069-IB16
1013 | RL7-BIN-103-ZSO-01 | [6 empty] | RL7-IPA1-RIO1 | 6 | 6 | 6 | 24 VDC DO | 5069-IB16
1014 | RL7-BIN-103-ZSC-01 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 6 | 7 | 24 VDC DO | 5069-IB16
1015 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 6 | 8 | 24 VDC DO | 5069-IB16
1016 | RL7-BIN-104-ZSO-01 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 6 | 9 | 24 VDC DO | 5069-IB16
1017 | RL7-BIN-104-ZSC-01 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 6 | 10 | 24 VDC DO | 5069-IB16
1018 | RL7-CNV-113-ZSO-01 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 6 | 11 | 24 VDC DO | 5069-IB16
1019 | RL7-CNV-113-ZSC-01 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 6 | 12 | 24 VDC DO | 5069-IB16
1020 | RL7-CNV-114-ZSO-08 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 6 | 13 | 24 VDC DO | 5069-IB16
1021 | RL7-CNV-114-ZSC-08 |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 6 | 14 | 24 VDC DO | 5069-IB16
1022 |  |  |  |  | SPARE |  |  | RL7-IPA1-RIO1 | 6 | 6 | 15 | 24 VDC DO | 5069-IB16
1023 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 2 | 6 | 24 VDC SI | 5069-IB8S
1024 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 2 | 7 | 24 VDC SI | 5069-IB8S
1025 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 4 | 0 | 24 VDC SI | 5069-IB8S
1026 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 4 | 1 | 24 VDC SI | 5069-IB8S
1027 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 4 | 2 | 24 VDC SI | 5069-IB8S
1028 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 4 | 3 | 24 VDC SI | 5069-IB8S
1029 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 4 | 4 | 24 VDC SI | 5069-IB8S
1030 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 4 | 5 | 24 VDC SI | 5069-IB8S
1031 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 4 | 6 | 24 VDC SI | 5069-IB8S
1032 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 4 | 7 | 24 VDC SI | 5069-IB8S
1033 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 5 | 0 | 24 VDC SO | 5069-OBV8S
1034 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 5 | 1 | 24 VDC SO | 5069-OBV8S
1035 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 5 | 2 | 24 VDC SO | 5069-OBV8S
1036 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 5 | 3 | 24 VDC SO | 5069-OBV8S
1037 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 5 | 4 | 24 VDC SO | 5069-OBV8S
1038 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 5 | 5 | 24 VDC SO | 5069-OBV8S
1039 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 5 | 6 | 24 VDC SO | 5069-OBV8S
1040 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 5 | 7 | 24 VDC SO | 5069-OBV8S
1041 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 6 | 8 | 24 VDC DI | 5069-IB16
1042 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 6 | 9 | 24 VDC DI | 5069-IB16
1043 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 6 | 10 | 24 VDC DI | 5069-IB16
1044 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 6 | 11 | 24 VDC DI | 5069-IB16
1045 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 6 | 12 | 24 VDC DI | 5069-IB16
1046 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 6 | 13 | 24 VDC DI | 5069-IB16
1047 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 6 | 14 | 24 VDC DI | 5069-IB16
1048 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 6 | 15 | 24 VDC DI | 5069-IB16
1049 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 5 | 24 VDC DO | 5069-OB16
1050 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 6 | 24 VDC DO | 5069-OB16
1051 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 7 | 24 VDC DO | 5069-OB16
1052 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 8 | 24 VDC DO | 5069-OB16
1053 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 9 | 24 VDC DO | 5069-OB16
1054 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 10 | 24 VDC DO | 5069-OB16
1055 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 11 | 24 VDC DO | 5069-OB16
1056 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 12 | 24 VDC DO | 5069-OB16
1057 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 13 | 24 VDC DO | 5069-OB16
1058 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 14 | 24 VDC DO | 5069-OB16
1059 |  |  |  |  | SPARE |  |  | RL7-IPA2-RIO1 | 7 | 7 | 15 | 24 VDC DO | 5069-OB16
1060 | [7 empty] | RL7-FAGC1-RIO1 | 8 | 3 | 2 | 24 VDC SI | 5069-IB8S
1061 | [7 empty] | RL7-FAGC1-RIO1 | 8 | 3 | 3 | 24 VDC SI | 5069-IB8S
1062 | [7 empty] | RL7-FAGC1-RIO1 | 8 | 3 | 4 | 24 VDC SI | 5069-IB8S
1063 | [7 empty] | RL7-FAGC1-RIO1 | 8 | 3 | 5 | 24 VDC SI | 5069-IB8S
1064 | [7 empty] | RL7-FAGC1-RIO1 | 8 | 3 | 6 | 24 VDC SI | 5069-IB8S
1065 | [7 empty] | RL7-FAGC1-RIO1 | 8 | 3 | 7 | 24 VDC SI | 5069-IB8S
1066 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 4 | 2 | 24 VDC DI | 5069-IB16
1067 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 4 | 4 | 24 VDC DI | 5069-IB16
1068 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 4 | 9 | 24 VDC DI | 5069-IB16
1069 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 4 | 10 | 24 VDC DI | 5069-IB16
1070 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 4 | 11 | 24 VDC DI | 5069-IB16
1071 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 4 | 12 | 24 VDC DI | 5069-IB16
1072 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 4 | 13 | 24 VDC DI | 5069-IB16
1073 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 4 | 14 | 24 VDC DI | 5069-IB16
1074 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 4 | 15 | 24 VDC DI | 5069-IB16
1075 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-FAGC1-RIO1 | 8 | 5 | 0 | ARM | 5069-ARM
1076 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 6 | 1 | 24 VDC DO | 5069-OB16
1077 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 6 | 9 | 24 VDC DO | 5069-OB16
1078 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 6 | 10 | 24 VDC DO | 5069-OB16
1079 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 6 | 11 | 24 VDC DO | 5069-OB16
1080 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 6 | 12 | 24 VDC DO | 5069-OB16
1081 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 6 | 13 | 24 VDC DO | 5069-OB16
1082 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 6 | 14 | 24 VDC DO | 5069-OB16
1083 |  |  |  |  | SPARE |  |  | RL7-FAGC1-RIO1 | 8 | 6 | 15 | 24 VDC DO | 5069-OB16
1084 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 3 | 2 | 24 VDC SI | 5069-IB8S
1085 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 3 | 3 | 24 VDC SI | 5069-IB8S
1086 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 3 | 4 | 24 VDC SI | 5069-IB8S
1087 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 3 | 5 | 24 VDC SI | 5069-IB8S
1088 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 3 | 6 | 24 VDC SI | 5069-IB8S
1089 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 3 | 7 | 24 VDC SI | 5069-IB8S
1090 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 4 | 2 | 24 VDC DI | 5069-IB16
1091 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 4 | 4 | 24 VDC DI | 5069-IB16
1092 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 4 | 9 | 24 VDC DI | 5069-IB16
1093 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 4 | 10 | 24 VDC DI | 5069-IB16
1094 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 4 | 11 | 24 VDC DI | 5069-IB16
1095 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 4 | 12 | 24 VDC DI | 5069-IB16
1096 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 4 | 13 | 24 VDC DI | 5069-IB16
1097 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 4 | 14 | 24 VDC DI | 5069-IB16
1098 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 4 | 15 | 24 VDC DI | 5069-IB16
1099 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-FAGC2-RIO1 | 9 | 5 | 0 | ARM | 5069-ARM
1100 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 6 | 1 | 24 VDC DO | 5069-OB16
1101 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 6 | 9 | 24 VDC DO | 5069-OB16
1102 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 6 | 10 | 24 VDC DO | 5069-OB16
1103 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 6 | 11 | 24 VDC DO | 5069-OB16
1104 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 6 | 12 | 24 VDC DO | 5069-OB16
1105 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 6 | 13 | 24 VDC DO | 5069-OB16
1106 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 6 | 14 | 24 VDC DO | 5069-OB16
1107 |  |  |  |  | SPARE |  |  | RL7-FAGC2-RIO1 | 9 | 6 | 15 | 24 VDC DO | 5069-OB16
1108 | RL7-CNV-107-ZSS-01 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 1 | 0 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1109 | RL7-CNV-107-ZSS-01 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 1 | 1 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1110 | RL7-CNV-107-ZSS-03 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 1 | 2 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1111 | RL7-CNV-107-ZSS-03 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 1 | 3 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1112 | RL7-CNV-107-ZSS-04 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 1 | 4 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1113 | RL7-CNV-107-ZSS-04 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 1 | 5 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1114 | RL7-CNV-107-ZSS-05 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 1 | 6 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1115 | RL7-CNV-107-ZSS-05 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 1 | 7 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1116 | RL7-CNV-107-ZSS-02 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 2 | 0 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1117 | RL7-CNV-107-ZSS-02 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 2 | 1 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1118 | RL7-CNV-107-ZSS-06 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 2 | 2 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1119 | RL7-CNV-107-ZSS-06 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 2 | 3 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1120 | RL7-CNV-107-ZSS-07 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 2 | 4 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1121 | RL7-CNV-107-ZSS-07 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 2 | 5 | 24 VDC SI | 5069-IB8S | [11 empty] | RESERVED FOR IPA3
1122 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 2 | 6 | 24 VDC SI | 5069-IB8S
1123 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 2 | 7 | 24 VDC SI | 5069-IB8S
1124 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 4 | 6 | 24 VDC SI | 5069-IB8S
1125 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 4 | 7 | 24 VDC SI | 5069-IB8S
1126 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 5 | 6 | 24 VDC SI | 5069-IB8S
1127 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 5 | 7 | 24 VDC SI | 5069-IB8S
1128 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 6 | 2 | 24 VDC SO | 5069-OBV8S
1129 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 6 | 3 | 24 VDC SO | 5069-OBV8S
1130 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 6 | 4 | 24 VDC SO | 5069-OBV8S
1131 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 6 | 5 | 24 VDC SO | 5069-OBV8S
1132 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 6 | 6 | 24 VDC SO | 5069-OBV8S
1133 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 6 | 7 | 24 VDC SO | 5069-OBV8S
1134 | RL7-MLT-106-ZSC-02 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 7 | 7 | 24 VDC DI | 5069-IB16
1135 | RL7-CNV-107-ZSC-06 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 8 | 0 | 24 VDC DI | 5069-IB16 | [11 empty] | RESERVED FOR IPA3
1136 | RL7-CNV-107-ZSC-03 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 8 | 1 | 24 VDC DI | 5069-IB16 | [11 empty] | RESERVED FOR IPA3
1137 | RL7-CNV-107-ZSC-04 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 8 | 2 | 24 VDC DI | 5069-IB16 | [11 empty] | RESERVED FOR IPA3
1138 | RL7-CNV-107-ZSC-02 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 8 | 3 | 24 VDC DI | 5069-IB16 | [11 empty] | RESERVED FOR IPA3
1139 | RL7-CNV-107-ZSC-05 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 8 | 4 | 24 VDC DI | 5069-IB16 | [11 empty] | RESERVED FOR IPA3
1140 | RL7-CNV-107-ZSC-07 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 8 | 5 | 24 VDC DI | 5069-IB16 | [11 empty] | RESERVED FOR IPA3
1141 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 8 | 13 | 24 VDC DI | 5069-IB16
1142 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 8 | 14 | 24 VDC DI | 5069-IB16
1143 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 8 | 15 | 24 VDC DI | 5069-IB16
1144 | RL7-CNV-107-XY-01 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 9 | 0 | 24 VDC DO | 5069-OB16 | [11 empty] | RESERVED FOR IPA3
1145 | RL7-CNV-107-XY-02 |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 9 | 1 | 24 VDC DO | 5069-OB16 | [11 empty] | RESERVED FOR IPA3
1146 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 9 | 15 | 24 VDC DO | 5069-OB16
1147 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 10 | 2 | 4-20 mA AI | 5069-IF8
1148 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 10 | 3 | 4-20 mA AI | 5069-IF8
1149 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 10 | 4 | 4-20 mA AI | 5069-IF8
1150 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 10 | 5 | 4-20 mA AI | 5069-IF8
1151 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 10 | 6 | 4-20 mA AI | 5069-IF8
1152 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 10 | 7 | 4-20 mA AI | 5069-IF8
1153 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 11 | 1 | 4-20 mA AO | 5069-OF8
1154 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 11 | 2 | 4-20 mA AO | 5069-OF8
1155 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 11 | 3 | 4-20 mA AO | 5069-OF8
1156 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 11 | 4 | 4-20 mA AO | 5069-OF8
1157 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 11 | 5 | 4-20 mA AO | 5069-OF8
1158 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 11 | 6 | 4-20 mA AO | 5069-OF8
1159 |  |  |  |  | SPARE |  |  | RL7-PRM-RIO1 | 10 | 11 | 7 | 4-20 mA AO | 5069-OF8
1160 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 1 | 6 | 24 VDC SI | 5069-IB8S
1161 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 1 | 7 | 24 VDC SI | 5069-IB8S
1162 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-BRED-RIO1 | 11 | 2 | 0 | ARM | 5069-ARM
1163 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 3 | 12 | 24 VDC DI | 5069-IB16
1164 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 3 | 13 | 24 VDC DI | 5069-IB16
1165 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 3 | 14 | 24 VDC DI | 5069-IB16
1166 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 3 | 15 | 24 VDC DI | 5069-IB16
1167 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 4 | 0 | 24 VDC DI | 5069-IB16
1168 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 4 | 1 | 24 VDC DI | 5069-IB16
1169 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 4 | 2 | 24 VDC DI | 5069-IB16
1170 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 4 | 3 | 24 VDC DI | 5069-IB16
1171 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 4 | 4 | 24 VDC DI | 5069-IB16
1172 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 4 | 13 | 24 VDC DI | 5069-IB16
1173 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 4 | 14 | 24 VDC DI | 5069-IB16
1174 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 4 | 15 | 24 VDC DI | 5069-IB16
1175 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 0 | 24 VDC DI | 5069-IB16
1176 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 1 | 24 VDC DI | 5069-IB16
1177 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 2 | 24 VDC DI | 5069-IB16
1178 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 3 | 24 VDC DI | 5069-IB16
1179 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 4 | 24 VDC DI | 5069-IB16
1180 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 5 | 24 VDC DI | 5069-IB16
1181 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 6 | 24 VDC DI | 5069-IB16
1182 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 7 | 24 VDC DI | 5069-IB16
1183 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 8 | 24 VDC DI | 5069-IB16
1184 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 9 | 24 VDC DI | 5069-IB16
1185 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 10 | 24 VDC DI | 5069-IB16
1186 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 11 | 24 VDC DI | 5069-IB16
1187 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 12 | 24 VDC DI | 5069-IB16
1188 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 13 | 24 VDC DI | 5069-IB16
1189 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 14 | 24 VDC DI | 5069-IB16
1190 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 5 | 15 | 24 VDC DI | 5069-IB16
1191 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 6 | 5 | 24 VDC DO | 5069-OB16
1192 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 6 | 6 | 24 VDC DO | 5069-OB16
1193 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 6 | 7 | 24 VDC DO | 5069-OB16
1194 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 6 | 8 | 24 VDC DO | 5069-OB16
1195 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 6 | 13 | 24 VDC DO | 5069-OB16
1196 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 6 | 14 | 24 VDC DO | 5069-OB16
1197 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 6 | 15 | 24 VDC DO | 5069-OB16
1198 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 7 | 0 | 24 VDC DO | 5069-OB16
1199 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 7 | 13 | 24 VDC DO | 5069-OB16
1200 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 7 | 14 | 24 VDC DO | 5069-OB16
1201 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 7 | 15 | 24 VDC DO | 5069-OB16
1202 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-BRED-RIO1 | 11 | 8 | 0 | ARM | 5069-ARM
1203 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 9 | 2 | 4-20 mA AI | 5069-IF8
1204 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 9 | 3 | 4-20 mA AI | 5069-IF8
1205 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 9 | 4 | 4-20 mA AI | 5069-IF8
1206 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 9 | 5 | 4-20 mA AI | 5069-IF8
1207 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 9 | 6 | 4-20 mA AI | 5069-IF8
1208 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 9 | 7 | 4-20 mA AI | 5069-IF8
1209 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 10 | 1 | 4-20 mA AO | 5069-OF8
1210 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 10 | 2 | 4-20 mA AO | 5069-OF8
1211 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 10 | 3 | 4-20 mA AO | 5069-OF8
1212 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 10 | 4 | 4-20 mA AO | 5069-OF8
1213 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 10 | 5 | 4-20 mA AO | 5069-OF8
1214 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 10 | 6 | 4-20 mA AO | 5069-OF8
1215 |  |  |  |  | SPARE |  |  | RL7-BRED-RIO1 | 11 | 10 | 7 | 4-20 mA AO | 5069-OF8
1216 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 1 | 2 | 24 VDC SI | 5069-IB8S
1217 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 1 | 3 | 24 VDC SI | 5069-IB8S
1218 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 1 | 6 | 24 VDC SI | 5069-IB8S
1219 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 1 | 7 | 24 VDC SI | 5069-IB8S
1220 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 3 | 6 | 24 VDC SI | 5069-IB8S
1221 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 3 | 7 | 24 VDC SI | 5069-IB8S
1222 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 4 | 2 | 24 VDC SO | 5069-OBV8S
1223 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 4 | 3 | 24 VDC SO | 5069-OBV8S
1224 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 4 | 4 | 24 VDC SO | 5069-OBV8S
1225 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 4 | 5 | 24 VDC SO | 5069-OBV8S
1226 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 4 | 6 | 24 VDC SO | 5069-OBV8S
1227 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 4 | 7 | 24 VDC SO | 5069-OBV8S
1228 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 5 | 9 | 24 VDC DI | 5069-IB16
1229 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 5 | 10 | 24 VDC DI | 5069-IB16
1230 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 5 | 11 | 24 VDC DI | 5069-IB16
1231 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 5 | 12 | 24 VDC DI | 5069-IB16
1232 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 5 | 13 | 24 VDC DI | 5069-IB16
1233 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 5 | 14 | 24 VDC DI | 5069-IB16
1234 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 5 | 15 | 24 VDC DI | 5069-IB16
1235 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 6 | 5 | 24 VDC DI | 5069-IB16
1236 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 6 | 10 | 24 VDC DI | 5069-IB16
1237 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 6 | 11 | 24 VDC DI | 5069-IB16
1238 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 6 | 12 | 24 VDC DI | 5069-IB16
1239 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 6 | 13 | 24 VDC DI | 5069-IB16
1240 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 6 | 14 | 24 VDC DI | 5069-IB16
1241 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 6 | 15 | 24 VDC DI | 5069-IB16
1242 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-CKR1-RIO1 | 12 | 7 | 0 | ARM | 5069-ARM
1243 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 8 | 8 | 24 VDC DO | 5069-OB16
1244 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 8 | 9 | 24 VDC DO | 5069-OB16
1245 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 8 | 10 | 24 VDC DO | 5069-OB16
1246 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 8 | 11 | 24 VDC DO | 5069-OB16
1247 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 8 | 12 | 24 VDC DO | 5069-OB16
1248 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 8 | 13 | 24 VDC DO | 5069-OB16
1249 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 8 | 14 | 24 VDC DO | 5069-OB16
1250 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 8 | 15 | 24 VDC DO | 5069-OB16
1251 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 9 | 10 | 24 VDC DO | 5069-OB16
1252 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 9 | 11 | 24 VDC DO | 5069-OB16
1253 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 9 | 12 | 24 VDC DO | 5069-OB16
1254 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 9 | 13 | 24 VDC DO | 5069-OB16
1255 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 9 | 14 | 24 VDC DO | 5069-OB16
1256 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 10 | 2 | 4-20 mA AI | 5069-IF8
1257 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 10 | 3 | 4-20 mA AI | 5069-IF8
1258 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 10 | 4 | 4-20 mA AI | 5069-IF8
1259 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 10 | 5 | 4-20 mA AI | 5069-IF8
1260 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 10 | 6 | 4-20 mA AI | 5069-IF8
1261 |  |  |  |  | SPARE |  |  | RL7-CKR1-RIO1 | 12 | 10 | 7 | 4-20 mA AI | 5069-IF8
1262 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 1 | 6 | 24 VDC SI | 5069-IB8S
1263 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 1 | 7 | 24 VDC SI | 5069-IB8S
1264 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 3 | 6 | 24 VDC SI | 5069-IB8S
1265 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 3 | 7 | 24 VDC SI | 5069-IB8S
1266 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 4 | 2 | 24 VDC SO | 5069-OBV8S
1267 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 4 | 3 | 24 VDC SO | 5069-OBV8S
1268 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 4 | 4 | 24 VDC SO | 5069-OBV8S
1269 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 4 | 5 | 24 VDC SO | 5069-OBV8S
1270 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 4 | 6 | 24 VDC SO | 5069-OBV8S
1271 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 4 | 7 | 24 VDC SO | 5069-OBV8S
1272 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 5 | 9 | 24 VDC DI | 5069-IB16
1273 | RL7-CNV-106-ZSO-08 |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 5 | 10 | 24 VDC DI | 5069-IB16
1274 | RL7-CNV-106-ZSC-08 |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 5 | 11 | 24 VDC DI | 5069-IB16
1275 | RL7-CNV-107-ZSO-08 | RL7-CNV-107-ZSO-08 |  |  | INCLINE PIVOT AUGER 3 SANITATION VALVE OPEN LIMIT SWITCH |  | PROC | RL7-CKR2-RIO1 | 13 | 5 | 14 | 24 VDC DI | 5069-IB16
1276 | RL7-CNV-107-ZSC-08 | RL7-CNV-107-ZSC-08 |  |  | INCLINE PIVOT AUGER 3 SANITATION VALVE CLOSED LIMIT SWITCH |  | PROC | RL7-CKR2-RIO1 | 13 | 5 | 15 | 24 VDC DI | 5069-IB16
1277 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 6 | 5 | 24 VDC DI | 5069-IB16
1278 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 6 | 10 | 24 VDC DI | 5069-IB16
1279 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 6 | 11 | 24 VDC DI | 5069-IB16
1280 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 6 | 12 | 24 VDC DI | 5069-IB16
1281 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 6 | 13 | 24 VDC DI | 5069-IB16
1282 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 6 | 14 | 24 VDC DI | 5069-IB16
1283 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 6 | 15 | 24 VDC DI | 5069-IB16
1284 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-CKR2-RIO1 | 13 | 7 | 0 | ARM | 5069-ARM
1285 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 8 | 8 | 24 VDC DO | 5069-OB16
1286 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 8 | 9 | 24 VDC DO | 5069-OB16
1287 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 8 | 10 | 24 VDC DO | 5069-OB16
1288 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 8 | 11 | 24 VDC DO | 5069-OB16
1289 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 8 | 12 | 24 VDC DO | 5069-OB16
1290 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 8 | 13 | 24 VDC DO | 5069-OB16
1291 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 8 | 15 | 24 VDC DO | 5069-OB16
1292 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 9 | 13 | 24 VDC DO | 5069-OB16
1293 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 9 | 14 | 24 VDC DO | 5069-OB16
1294 | RL7-CKR-102-XY-24 | [6 empty] | RL7-CKR2-RIO1 | 13 | 9 | 15 | 24 VDC DO | 5069-OB16
1295 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 10 | 2 | 4-20 mA AI | 5069-IF8
1296 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 10 | 3 | 4-20 mA AI | 5069-IF8
1297 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 10 | 4 | 4-20 mA AI | 5069-IF8
1298 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 10 | 5 | 4-20 mA AI | 5069-IF8
1299 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 10 | 6 | 4-20 mA AI | 5069-IF8
1300 |  |  |  |  | SPARE |  |  | RL7-CKR2-RIO1 | 13 | 10 | 7 | 4-20 mA AI | 5069-IF8
1301 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 1 | 6 | 24 VDC SI | 5069-IB8S
1302 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 1 | 7 | 24 VDC SI | 5069-IB8S
1303 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 2 | 4 | 24 VDC SI | 5069-IB8S
1304 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 2 | 5 | 24 VDC SI | 5069-IB8S
1305 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 2 | 6 | 24 VDC SI | 5069-IB8S
1306 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 2 | 7 | 24 VDC SI | 5069-IB8S
1307 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 3 | 2 | 24 VDC SO | 5069-OBV8S
1308 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 3 | 3 | 24 VDC SO | 5069-OBV8S
1309 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 3 | 4 | 24 VDC SO | 5069-OBV8S
1310 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 3 | 5 | 24 VDC SO | 5069-OBV8S
1311 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 3 | 6 | 24 VDC SO | 5069-OBV8S
1312 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 3 | 7 | 24 VDC SO | 5069-OBV8S
1313 | RL7-AGC-201-ZSC-03 |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 4 | 3 | 24 VDC DI | 5069-IB16
1314 | RL7-AGC-201-ZSC-04 |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 4 | 4 | 24 VDC DI | 5069-IB16
1315 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 4 | 5 | 24 VDC DI | 5069-IB16
1316 | RL7-AGC-201-HS-01B |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 4 | 9 | 24 VDC DI | 5069-IB16
1317 | RL7-AGC-201-PB-02 |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 4 | 10 | 24 VDC DI | 5069-IB16
1318 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 4 | 11 | 24 VDC DI | 5069-IB16
1319 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 4 | 12 | 24 VDC DI | 5069-IB16
1320 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 4 | 13 | 24 VDC DI | 5069-IB16
1321 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 4 | 14 | 24 VDC DI | 5069-IB16
1322 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 4 | 15 | 24 VDC DI | 5069-IB16
1323 | RL7-AGC-201-PB-02 |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 5 | 10 | 24 VDC DI | 5069-IB16
1324 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 5 | 11 | 24 VDC DI | 5069-IB16
1325 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 5 | 12 | 24 VDC DI | 5069-IB16
1326 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 5 | 13 | 24 VDC DI | 5069-IB16
1327 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 5 | 14 | 24 VDC DI | 5069-IB16
1328 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 5 | 15 | 24 VDC DI | 5069-IB16
1329 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-DAGC1-RIO1 | 14 | 6 | 0 | ARM | 5069-ARM
1330 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 7 | 1 | 24 VDC DO | 5069-OB16
1331 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 7 | 9 | 24 VDC DO | 5069-OB16
1332 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 7 | 10 | 24 VDC DO | 5069-OB16
1333 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 7 | 11 | 24 VDC DO | 5069-OB16
1334 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 8 | 4 | 4-20 mA AI | 5069-IF8
1335 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 8 | 5 | 4-20 mA AI | 5069-IF8
1336 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 8 | 6 | 4-20 mA AI | 5069-IF8
1337 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 8 | 7 | 4-20 mA AI | 5069-IF8
1338 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 9 | 1 | 4-20 mA AO | 5069-OF8
1339 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 9 | 2 | 4-20 mA AO | 5069-OF8
1340 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 9 | 3 | 4-20 mA AO | 5069-OF8
1341 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 9 | 4 | 4-20 mA AO | 5069-OF8
1342 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 9 | 5 | 4-20 mA AO | 5069-OF8
1343 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 9 | 6 | 4-20 mA AO | 5069-OF8
1344 |  |  |  |  | SPARE |  |  | RL7-DAGC1-RIO1 | 14 | 9 | 7 | 4-20 mA AO | 5069-OF8
1345 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 1 | 0 | 24 VDC SI | 5069-IB8S
1346 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 1 | 1 | 24 VDC SI | 5069-IB8S
1347 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 2 | 0 | 24 VDC SI | 5069-IB8S
1348 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 2 | 1 | 24 VDC SI | 5069-IB8S
1349 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 2 | 4 | 24 VDC SI | 5069-IB8S
1350 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 2 | 5 | 24 VDC SI | 5069-IB8S
1351 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 2 | 6 | 24 VDC SI | 5069-IB8S
1352 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 2 | 7 | 24 VDC SI | 5069-IB8S
1353 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 3 | 6 | 24 VDC DI | 5069-IB16
1354 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 3 | 10 | 24 VDC DI | 5069-IB16
1355 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 3 | 24 VDC DI | 5069-IB16
1356 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 4 | 24 VDC DI | 5069-IB16
1357 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 5 | 24 VDC DI | 5069-IB16
1358 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 6 | 24 VDC DI | 5069-IB16
1359 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 7 | 24 VDC DI | 5069-IB16
1360 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 8 | 24 VDC DI | 5069-IB16
1361 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 9 | 24 VDC DI | 5069-IB16
1362 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 10 | 24 VDC DI | 5069-IB16
1363 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 11 | 24 VDC DI | 5069-IB16
1364 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 12 | 24 VDC DI | 5069-IB16
1365 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 13 | 24 VDC DI | 5069-IB16
1366 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 14 | 24 VDC DI | 5069-IB16
1367 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 4 | 15 | 24 VDC DI | 5069-IB16
1368 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 5 | 5 | 24 VDC DO | 5069-OB16
1369 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 5 | 7 | 24 VDC DO | 5069-OB16
1370 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 4 | 24 VDC DO | 5069-OB16
1371 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 5 | 24 VDC DO | 5069-OB16
1372 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 6 | 24 VDC DO | 5069-OB16
1373 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 7 | 24 VDC DO | 5069-OB16
1374 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 8 | 24 VDC DO | 5069-OB16
1375 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 9 | 24 VDC DO | 5069-OB16
1376 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 10 | 24 VDC DO | 5069-OB16
1377 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 11 | 24 VDC DO | 5069-OB16
1378 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 12 | 24 VDC DO | 5069-OB16
1379 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 13 | 24 VDC DO | 5069-OB16
1380 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 14 | 24 VDC DO | 5069-OB16
1381 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 6 | 15 | 24 VDC DO | 5069-OB16
1382 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 7 | 7 | 4-20 mA AI | 5069-IF8
1383 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 8 | 7 | 4-20 mA AI | 5069-IF8
1384 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 9 | 0 | 4-20 mA AO | 5069-OF8
1385 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 9 | 1 | 4-20 mA AO | 5069-OF8
1386 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 9 | 2 | 4-20 mA AO | 5069-OF8
1387 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 9 | 3 | 4-20 mA AO | 5069-OF8
1388 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 9 | 4 | 4-20 mA AO | 5069-OF8
1389 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 9 | 5 | 4-20 mA AO | 5069-OF8
1390 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 9 | 6 | 4-20 mA AO | 5069-OF8
1391 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO1 | 15 | 9 | 7 | 4-20 mA AO | 5069-OF8
1392 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 1 | 6 | 24 VDC SI | 5069-IB8S
1393 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 1 | 7 | 24 VDC SI | 5069-IB8S
1394 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-SERP-RIO2 | 16 | 2 | 0 | ARM | 5069-ARM
1395 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 4 | 24 VDC DI | 5069-IB16
1396 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 5 | 24 VDC DI | 5069-IB16
1397 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 6 | 24 VDC DI | 5069-IB16
1398 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 7 | 24 VDC DI | 5069-IB16
1399 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 8 | 24 VDC DI | 5069-IB16
1400 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 9 | 24 VDC DI | 5069-IB16
1401 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 10 | 24 VDC DI | 5069-IB16
1402 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 11 | 24 VDC DI | 5069-IB16
1403 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 12 | 24 VDC DI | 5069-IB16
1404 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 13 | 24 VDC DI | 5069-IB16
1405 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 14 | 24 VDC DI | 5069-IB16
1406 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 3 | 15 | 24 VDC DI | 5069-IB16
1407 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-SERP-RIO2 | 16 | 4 | 0 | ARM | 5069-ARM
1408 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 0 | 24 VDC DO | 5069-OB16
1409 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 1 | 24 VDC DO | 5069-OB16
1410 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 2 | 24 VDC DO | 5069-OB16
1411 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 3 | 24 VDC DO | 5069-OB16
1412 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 4 | 24 VDC DO | 5069-OB16
1413 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 5 | 24 VDC DO | 5069-OB16
1414 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 6 | 24 VDC DO | 5069-OB16
1415 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 7 | 24 VDC DO | 5069-OB16
1416 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 8 | 24 VDC DO | 5069-OB16
1417 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 9 | 24 VDC DO | 5069-OB16
1418 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 10 | 24 VDC DO | 5069-OB16
1419 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 5 | 15 | 24 VDC DO | 5069-OB16
1420 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-SERP-RIO2 | 16 | 6 | 0 | ARM | 5069-ARM
1421 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 8 | 3 | 4-20 mA AI | 5069-IF8
1422 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 8 | 4 | 4-20 mA AI | 5069-IF8
1423 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 8 | 5 | 4-20 mA AI | 5069-IF8
1424 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 8 | 6 | 4-20 mA AI | 5069-IF8
1425 |  |  |  |  | SPARE |  |  | RL7-SERP-RIO2 | 16 | 8 | 7 | 4-20 mA AI | 5069-IF8
1426 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-SERP-RIO2 | 16 | 9 | 0 | ARM | 5069-ARM
1427 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 1 | 9 | 24 VDC DI | 5069-OBV8S
1428 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 1 | 10 | 24 VDC DI | 5069-OBV8S
1429 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 1 | 11 | 24 VDC DI | 5069-OBV8S
1430 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 1 | 12 | 24 VDC DI | 5069-OBV8S
1431 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 1 | 13 | 24 VDC DI | 5069-OBV8S
1432 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 1 | 14 | 24 VDC DI | 5069-OBV8S
1433 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 1 | 15 | 24 VDC DI | 5069-OBV8S
1434 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-PKOUT-RIO1 | 17 | 2 | 0 | ARM | 5069-ARM
1435 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 2 | 24 VDC DO | 5069-OBV8S
1436 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 3 | 24 VDC DO | 5069-OBV8S
1437 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 4 | 24 VDC DO | 5069-OBV8S
1438 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 5 | 24 VDC DO | 5069-OBV8S
1439 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 6 | 24 VDC DO | 5069-OBV8S
1440 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 7 | 24 VDC DO | 5069-OBV8S
1441 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 8 | 24 VDC DO | 5069-OBV8S
1442 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 9 | 24 VDC DO | 5069-OBV8S
1443 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 10 | 24 VDC DO | 5069-OBV8S
1444 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 11 | 24 VDC DO | 5069-OBV8S
1445 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 12 | 24 VDC DO | 5069-OBV8S
1446 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 13 | 24 VDC DO | 5069-OBV8S
1447 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 14 | 24 VDC DO | 5069-OBV8S
1448 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 3 | 15 | 24 VDC DO | 5069-OBV8S
1449 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 4 | 0 | 4-20 mA AI | 5069-OB16
1450 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 4 | 1 | 4-20 mA AI | 5069-OB16
1451 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 4 | 2 | 4-20 mA AI | 5069-OB16
1452 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 4 | 3 | 4-20 mA AI | 5069-OB16
1453 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 4 | 4 | 4-20 mA AI | 5069-OB16
1454 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 4 | 5 | 4-20 mA AI | 5069-OB16
1455 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 4 | 6 | 4-20 mA AI | 5069-OB16
1456 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 4 | 7 | 4-20 mA AI | 5069-OB16
1457 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-PKOUT-RIO1 | 17 | 5 | 0 | ARM | 5069-ARM
1458 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 6 | 0 | 4-20 mA AO | 5069-OB16
1459 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 6 | 1 | 4-20 mA AO | 5069-OB16
1460 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 6 | 2 | 4-20 mA AO | 5069-OB16
1461 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 6 | 3 | 4-20 mA AO | 5069-OB16
1462 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 6 | 4 | 4-20 mA AO | 5069-OB16
1463 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 6 | 5 | 4-20 mA AO | 5069-OB16
1464 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 6 | 6 | 4-20 mA AO | 5069-OB16
1465 |  |  |  |  | SPARE |  |  | RL7-PKOUT-RIO1 | 17 | 6 | 7 | 4-20 mA AO | 5069-OB16
1466 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 1 | 10 | 24 VDC DI | 5069-IB16
1467 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 1 | 11 | 24 VDC DI | 5069-IB16
1468 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 1 | 12 | 24 VDC DI | 5069-IB16
1469 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 1 | 13 | 24 VDC DI | 5069-IB16
1470 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 1 | 14 | 24 VDC DI | 5069-IB16
1471 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 1 | 15 | 24 VDC DI | 5069-IB16
1472 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 2 | 10 | 24 VDC DI | 5069-IB16
1473 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 2 | 11 | 24 VDC DI | 5069-IB16
1474 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 2 | 12 | 24 VDC DI | 5069-IB16
1475 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 2 | 13 | 24 VDC DI | 5069-IB16
1476 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 2 | 14 | 24 VDC DI | 5069-IB16
1477 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 2 | 15 | 24 VDC DI | 5069-IB16
1478 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 3 | 9 | 24 VDC DO | 5069-OB16
1479 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 3 | 10 | 24 VDC DO | 5069-OB16
1480 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 3 | 11 | 24 VDC DO | 5069-OB16
1481 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 3 | 12 | 24 VDC DO | 5069-OB16
1482 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 3 | 13 | 24 VDC DO | 5069-OB16
1483 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 3 | 14 | 24 VDC DO | 5069-OB16
1484 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 3 | 15 | 24 VDC DO | 5069-OB16
1485 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 5 | 24 VDC DO | 5069-OB16
1486 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 6 | 24 VDC DO | 5069-OB16
1487 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 7 | 24 VDC DO | 5069-OB16
1488 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 8 | 24 VDC DO | 5069-OB16
1489 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 9 | 24 VDC DO | 5069-OB16
1490 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 10 | 24 VDC DO | 5069-OB16
1491 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 11 | 24 VDC DO | 5069-OB16
1492 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 12 | 24 VDC DO | 5069-OB16
1493 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 13 | 24 VDC DO | 5069-OB16
1494 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 14 | 24 VDC DO | 5069-OB16
1495 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 4 | 15 | 24 VDC DO | 5069-OB16
1496 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-INTSL-RIO1 | 18 | 5 | 0 | ARM | 5069-ARM
1497 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 6 | 6 | 4-20 mA AI | 5069-IF8
1498 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 6 | 7 | 4-20 mA AI | 5069-IF8
1499 |  | RL7-LINE-FIT-03 | M2A-4 |  | LINE PHWS140 FLOW |  |  | RL7-INTSL-RIO1 | 18 | 7 | 6 | 4-20 mA AI | 5069-IF8 | 0 - 125 GPM
1500 |  | RL7-LINE-FIT-05 | M2A-6 |  | LINE PHWR140 FLOW |  |  | RL7-INTSL-RIO1 | 18 | 7 | 7 | 4-20 mA AI | 5069-IF8 | 0 - 125 GPM
1501 |  | RL7-LINE-FIT-01 | M2A-2 |  | LINE PCW FLOW |  | INTSL | RL7-INTSL-RIO1 | 18 | 8 | 4 | 4-20 mA AI | 5069-IF8 | 0 - 650 GPM
1502 |  | RL7-LINE-FIT-02 | M2A-3 |  | LINE HPWS FLOW |  | INTSL | RL7-INTSL-RIO1 | 18 | 8 | 5 | 4-20 mA AI | 5069-IF8 | 0 - 250 GPM
1503 |  | RL7-LINE-FIT-04 | M2A-5 |  | LINE HPWR FLOW |  | INTSL | RL7-INTSL-RIO1 | 18 | 8 | 6 | 4-20 mA AI | 5069-IF8 | 0 - 250 GPM
1504 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 8 | 7 | 4-20 mA AI | 5069-IF8
1505 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 9 | 4 | 4-20 mA AI | 5069-IF8 | [11 empty] | MULTI-VARIABLE XMTR, INCLUDES PRESSURE & TEMP
1506 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 9 | 5 | 4-20 mA AI | 5069-IF8 | [11 empty] | MULTI-VARIABLE XMTR, INCLUDES PRESSURE & TEMP
1507 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 9 | 6 | 4-20 mA AI | 5069-IF8 | [11 empty] | MULTI-VARIABLE XMTR, INCLUDES PRESSURE & TEMP
1508 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 9 | 7 | 4-20 mA AI | 5069-IF8
1509 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 10 | 5 | 4-20 mA AI | 5069-IF8 | [11 empty] | MULTI-VARIABLE XMTR, INCLUDES PRESSURE & TEMP
1510 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 10 | 6 | 4-20 mA AI | 5069-IF8 | [11 empty] | MULTI-VARIABLE XMTR, INCLUDES PRESSURE & TEMP
1511 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 10 | 7 | 4-20 mA AI | 5069-IF8
1512 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-INTSL-RIO1 | 18 | 11 | 0 | ARM | 5069-ARM
1513 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 12 | 4 | 4-20 mA AO | 5069-OF8
1514 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 12 | 5 | 4-20 mA AO | 5069-OF8
1515 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 12 | 6 | 4-20 mA AO | 5069-OF8
1516 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 12 | 7 | 4-20 mA AO | 5069-OF8
1517 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 13 | 4 | 4-20 mA AO | 5069-OF8
1518 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 13 | 5 | 4-20 mA AO | 5069-OF8
1519 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 13 | 6 | 4-20 mA AO | 5069-OF8
1520 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 13 | 7 | 4-20 mA AO | 5069-OF8
1521 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 14 | 10 | 24 VDC DO | 5069-OB16
1522 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 14 | 11 | 24 VDC DO | 5069-OB16
1523 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 14 | 12 | 24 VDC DO | 5069-OB16
1524 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 14 | 13 | 24 VDC DO | 5069-OB16
1525 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 14 | 14 | 24 VDC DO | 5069-OB16
1526 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 14 | 15 | 24 VDC DO | 5069-OB16
1527 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 15 | 2 | 24 VDC SI | 5069-IB8S
1528 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 15 | 3 | 24 VDC SI | 5069-IB8S
1529 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 15 | 4 | 24 VDC SI | 5069-IB8S
1530 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 15 | 5 | 24 VDC SI | 5069-IB8S
1531 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 15 | 6 | 24 VDC SI | 5069-IB8S
1532 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO1 | 18 | 15 | 7 | 24 VDC SI | 5069-IB8S
1533 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 2 | 12 | 24 VDC DI | 5069-IB16
1534 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 2 | 13 | 24 VDC DI | 5069-IB16
1535 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 2 | 14 | 24 VDC DI | 5069-IB16
1536 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 2 | 15 | 24 VDC DI | 5069-IB16
1537 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 3 | 12 | 24 VDC DI | 5069-IB16
1538 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 3 | 13 | 24 VDC DI | 5069-IB16
1539 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 3 | 14 | 24 VDC DI | 5069-IB16
1540 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 3 | 15 | 24 VDC DI | 5069-IB16
1541 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-INTSL-RIO2 | 19 | 4 | 0 | ARM | 5069-ARM
1542 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 5 | 14 | 24 VDC DO | 5069-OB16
1543 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 5 | 15 | 24 VDC DO | 5069-OB16
1544 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 6 | 8 | 24 VDC DO | 5069-OB16
1545 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 6 | 9 | 24 VDC DO | 5069-OB16
1546 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 6 | 10 | 24 VDC DO | 5069-OB16
1547 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 6 | 11 | 24 VDC DO | 5069-OB16
1548 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 6 | 12 | 24 VDC DO | 5069-OB16
1549 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 6 | 13 | 24 VDC DO | 5069-OB16
1550 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 6 | 14 | 24 VDC DO | 5069-OB16
1551 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 6 | 15 | 24 VDC DO | 5069-OB16
1552 | RL7-CHR-201-XV-03 |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 4 | 24 VDC DO | 5069-OB16
1553 | RL7-CHR-201-XV-04 |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 5 | 24 VDC DO | 5069-OB16
1554 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 6 | 24 VDC DO | 5069-OB16
1555 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 7 | 24 VDC DO | 5069-OB16
1556 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 8 | 24 VDC DO | 5069-OB16
1557 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 9 | 24 VDC DO | 5069-OB16
1558 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 10 | 24 VDC DO | 5069-OB16
1559 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 11 | 24 VDC DO | 5069-OB16
1560 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 12 | 24 VDC DO | 5069-OB16
1561 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 13 | 24 VDC DO | 5069-OB16
1562 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 14 | 24 VDC DO | 5069-OB16
1563 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 7 | 15 | 24 VDC DO | 5069-OB16
1564 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-INTSL-RIO2 | 19 | 8 | 0 | ARM | 5069-ARM
1565 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 9 | 7 | 4-20 mA AI | 5069-IF8
1566 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 10 | 3 | 4-20 mA AI | 5069-IF8
1567 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 10 | 4 | 4-20 mA AI | 5069-IF8
1568 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 10 | 5 | 4-20 mA AI | 5069-IF8
1569 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 10 | 6 | 4-20 mA AI | 5069-IF8
1570 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 10 | 7 | 4-20 mA AI | 5069-IF8
1571 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 11 | 3 | 4-20 mA AI | 5069-IF8
1572 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 11 | 4 | 4-20 mA AI | 5069-IF8
1573 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 11 | 5 | 4-20 mA AI | 5069-IF8
1574 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 11 | 6 | 4-20 mA AI | 5069-IF8
1575 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 11 | 7 | 4-20 mA AI | 5069-IF8
1576 |  |  |  |  | ADDRESS RESERVE MODULE |  |  | RL7-INTSL-RIO2 | 19 | 12 | 0 | ARM | 5069-ARM
1577 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 13 | 4 | 4-20 mA AO | 5069-OF8
1578 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 13 | 5 | 4-20 mA AO | 5069-OF8
1579 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 13 | 6 | 4-20 mA AO | 5069-OF8
1580 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 13 | 7 | 4-20 mA AO | 5069-OF8
1581 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 14 | 1 | I/V/T AI | 5069-IY4
1582 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 14 | 2 | I/V/T AI | 5069-IY4
1583 |  |  |  |  | SPARE |  |  | RL7-INTSL-RIO2 | 19 | 14 | 3 | I/V/T AI | 5069-IY4
1584 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 0 | 6 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1585 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 0 | 7 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1586 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 0 | 8 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1587 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 0 | 9 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1588 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 0 | 10 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1589 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 0 | 11 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1590 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 0 | 12 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1591 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 0 | 13 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1592 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 0 | 14 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1593 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 0 | 15 | 24 VDC DI | 5069-IB16 | [11 empty] | OEM PANEL
1594 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 3 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1595 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 4 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1596 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 5 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1597 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 6 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1598 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 7 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1599 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 8 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1600 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 9 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1601 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 10 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1602 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 11 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1603 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 12 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1604 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 13 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1605 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 14 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1606 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 1 | 15 | 24 VDC DO | 5069-OB16 | [11 empty] | OEM PANEL
1607 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 3 | 1 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
1608 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 3 | 2 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
1609 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 3 | 3 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
1610 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 3 | 4 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
1611 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 3 | 5 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
1612 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 3 | 6 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
1613 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 3 | 7 | 4-20 mA AI | 5069-IF8 | [11 empty] | OEM PANEL
1614 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 4 | 1 | 4-20 mA AO | 5069-OF8 | [11 empty] | OEM PANEL
1615 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 4 | 2 | 4-20 mA AO | 5069-OF8 | [11 empty] | OEM PANEL
1616 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 4 | 3 | 4-20 mA AO | 5069-OF8 | [11 empty] | OEM PANEL
1617 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 4 | 4 | 4-20 mA AO | 5069-OF8 | [11 empty] | OEM PANEL
1618 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 4 | 5 | 4-20 mA AO | 5069-OF8 | [11 empty] | OEM PANEL
1619 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 4 | 6 | 4-20 mA AO | 5069-OF8 | [11 empty] | OEM PANEL
1620 |  |  |  |  | SPARE |  |  | RL7-DXPHX-RIO1 | 20 | 4 | 7 | 4-20 mA AO | 5069-OF8 | [11 empty] | OEM PANEL
|  | I/O TOTALS | [10 empty] | --------- | ------------ | DEVICE INSTALLED | DEVICE TAGGED | CA INSTALLED | RACEWAYS COMPLETE | WIRE PULLED | WIRE TERMED | WIRE TAGGED | POINT TO POINT | IO CHECK | IO GOOD
|  | 24 VDC SI | 218 | [9 empty] | COMPLETED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 24 VDC SO | 8 | [9 empty] | TOTAL |  | 830 | 830 | 176 | 830 | 830 | 830 | 830 | 830 | 830 | 0
|  | 24 VDC DI | 256 | [9 empty] | % COMPLETE |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | 24 VDC DO | 242 | [9 empty] | % REMAINING |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | 4-20 mA AI | 89
|  | 4-20 mA AO | 16 | [9 empty] | PROCESSING
|  | I/V/T AI | 1 | [9 empty] | COMPLETED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 512 | 512 | 99 | 512 | 512 | 512 | 512 | 512 | 512 | 0
|  | RL7 TOTAL | 830 | [9 empty] | % COMPLETE |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[13 empty] | % REMAINING |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
CHILLING
[13 empty] | COMPLETED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 128 | 128 | 20 | 128 | 128 | 128 | 128 | 128 | 128 | 0
[13 empty] | % COMPLETE |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[13 empty] | % REMAINING |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
INTERSTITIAL
[13 empty] | COMPLETED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 156 | 156 | 51 | 156 | 156 | 156 | 156 | 156 | 156 | 0
[13 empty] | % COMPLETE |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[13 empty] | % REMAINING |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
HEAT EXCHANGER / LACTIC ACID
[13 empty] | COMPLETED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 22 | 22 | 6 | 22 | 22 | 22 | 22 | 22 | 22 | 0
[13 empty] | % COMPLETE |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[13 empty] | % REMAINING |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
MCC
[13 empty] | COMPLETED |  | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 10 | 10 | N/A | 10 | 10 | 10 | 10 | 10 | 10 | 0
[13 empty] | % COMPLETE |  | 0% | 0% | N/A | 0% | 0% | 0% | 0% | 0% | 0% | 0%
[13 empty] | % REMAINING |  | 100% | 100% | N/A | 100% | 100% | 100% | 100% | 100% | 100% | 100%

## UTIL
NO | PHASE 2 TAG | PHASE 2A TAG | OEM TAGNAME | JB | DESCRIPTION | P&ID | ROOM | PANEL | ORDER | SLOT | CH | MODULE TYPE | MODULE P/N | RANGE | DEVICE INSTALLED | DEVICE TAGGED | CA INSTALLED | RACEWAYS COMPLETE | WIRE PULLED | WIRE TERMED | WIRE TAGGED | POINT TO POINT | IO CHECK | IO GOOD | NOTES
[9 empty] | 0 | 0 | 0
1 | RL-TNK-201-ZSO-01 |  |  |  | FOAM TANK REFILL VALVE OPEN LIMIT SWITCH | DG6826 | HX / LA | PROD-UTIL-PLC2 | 0 | 1 | 0 | 24 VDC DI | 5069-IB16
2 | RL-TNK-201-ZSC-01 |  |  |  | FOAM TANK REFILL VALVE CLOSED LIMIT SWITCH | DG6826 | HX / LA | PROD-UTIL-PLC2 | 0 | 1 | 1 | 24 VDC DI | 5069-IB16
3 | RL-TNK-201-LSL-01 |  |  |  | FOAM TANK LOW LEVEL | DG6826 | HX / LA | PROD-UTIL-PLC2 | 0 | 1 | 2 | 24 VDC DI | 5069-IB16
4 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 3 | 24 VDC DI | 5069-IB16
5 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 4 | 24 VDC DI | 5069-IB16
6 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 5 | 24 VDC DI | 5069-IB16
7 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 6 | 24 VDC DI | 5069-IB16
8 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 7 | 24 VDC DI | 5069-IB16
9 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 8 | 24 VDC DI | 5069-IB16
10 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 9 | 24 VDC DI | 5069-IB16
11 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 10 | 24 VDC DI | 5069-IB16
12 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 11 | 24 VDC DI | 5069-IB16
13 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 12 | 24 VDC DI | 5069-IB16
14 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 13 | 24 VDC DI | 5069-IB16
15 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 14 | 24 VDC DI | 5069-IB16
16 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 1 | 15 | 24 VDC DI | 5069-IB16
17 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 0 | 24 VDC DI | 5069-IB16
18 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 1 | 24 VDC DI | 5069-IB16
19 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 2 | 24 VDC DI | 5069-IB16
20 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 3 | 24 VDC DI | 5069-IB16
21 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 4 | 24 VDC DI | 5069-IB16
22 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 5 | 24 VDC DI | 5069-IB16
23 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 6 | 24 VDC DI | 5069-IB16
24 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 7 | 24 VDC DI | 5069-IB16
25 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 8 | 24 VDC DI | 5069-IB16
26 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 9 | 24 VDC DI | 5069-IB16
27 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 10 | 24 VDC DI | 5069-IB16
28 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 11 | 24 VDC DI | 5069-IB16
29 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 12 | 24 VDC DI | 5069-IB16
30 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 13 | 24 VDC DI | 5069-IB16
31 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 14 | 24 VDC DI | 5069-IB16
32 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 2 | 15 | 24 VDC DI | 5069-IB16
33 | RL-TNK-201-XV-01 |  |  |  | FOAM TANK REFILL VALVE OPEN SOLENOID | DG6826 | HX / LA | PROD-UTIL-PLC2 | 0 | 3 | 0 | 24 VDC DO | 5069-OB16
34 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 1 | 24 VDC DO | 5069-OB16
35 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 2 | 24 VDC DO | 5069-OB16
36 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 3 | 24 VDC DO | 5069-OB16
37 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 4 | 24 VDC DO | 5069-OB16
38 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 5 | 24 VDC DO | 5069-OB16
39 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 6 | 24 VDC DO | 5069-OB16
40 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 7 | 24 VDC DO | 5069-OB16
41 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 8 | 24 VDC DO | 5069-OB16
42 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 9 | 24 VDC DO | 5069-OB16
43 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 10 | 24 VDC DO | 5069-OB16
44 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 11 | 24 VDC DO | 5069-OB16
45 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 12 | 24 VDC DO | 5069-OB16
46 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 13 | 24 VDC DO | 5069-OB16
47 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 14 | 24 VDC DO | 5069-OB16
48 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 3 | 15 | 24 VDC DO | 5069-OB16
49 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 0 | 24 VDC DO | 5069-OB16
50 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 1 | 24 VDC DO | 5069-OB16
51 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 2 | 24 VDC DO | 5069-OB16
52 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 3 | 24 VDC DO | 5069-OB16
53 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 4 | 24 VDC DO | 5069-OB16
54 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 5 | 24 VDC DO | 5069-OB16
55 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 6 | 24 VDC DO | 5069-OB16
56 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 7 | 24 VDC DO | 5069-OB16
57 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 8 | 24 VDC DO | 5069-OB16
58 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 9 | 24 VDC DO | 5069-OB16
59 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 10 | 24 VDC DO | 5069-OB16
60 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 11 | 24 VDC DO | 5069-OB16
61 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 12 | 24 VDC DO | 5069-OB16
62 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 13 | 24 VDC DO | 5069-OB16
63 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 14 | 24 VDC DO | 5069-OB16
64 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 4 | 15 | 24 VDC DO | 5069-OB16
65 | RL-WSH-101-PIT-01 |  |  |  | PHASE 2 TOTE WASHER HPS PRESSURE | DG6927 | INTSL | PROD-UTIL-PLC2 | 0 | 5 | 0 | 4-20 mA AI | 5069-IF8
66 | RL-CKR-100-PIT-101 |  |  |  | PHASE 2 COOKERS HPS HEADER PRESSURE | DG6927 | INTSL | PROD-UTIL-PLC2 | 0 | 5 | 1 | 4-20 mA AI | 5069-IF8
67 | CVI-1 |  |  |  | PHASE 1 / 2 COMPRESSED AIR JUMPER VALVE POSITION FEEDBACK |  | INTSL | PROD-UTIL-PLC2 | 0 | 5 | 2 | 4-20 mA AI | 5069-IF8
68 | CVI-2 |  |  |  | PHASE 1 / 2 HIGH PRESSURE HOT WATER SUPPLY JUMPER VALVE POSITION FEEDBACK |  | INTSL | PROD-UTIL-PLC2 | 0 | 5 | 3 | 4-20 mA AI | 5069-IF8
69 | CVI-3 |  |  |  | PHASE 1 / 2 PROCESS HOT WATER SUPPLY JUMPER VALVE POSITION FEEDBACK |  | INTSL | PROD-UTIL-PLC2 | 0 | 5 | 4 | 4-20 mA AI | 5069-IF8
70 | CVI-5 |  |  |  | PHASE 1 / 2 PROCESS HOT WATER RETURN JUMPER VALVE POSITION FEEDBACK |  | INTSL | PROD-UTIL-PLC2 | 0 | 5 | 5 | 4-20 mA AI | 5069-IF8
71 | CVI-7 |  |  |  | PHASE 1 / 2 HIGH PRESSURE HOT WATER RETURN JUMPER VALVE POSITION FEEDBACK |  | INTSL | PROD-UTIL-PLC2 | 0 | 5 | 6 | 4-20 mA AI | 5069-IF8
72 | RL-TNK-201-LIT-01 |  |  |  | FOAM TANK LEVEL INDICATION | DG6826 | INTSL | PROD-UTIL-PLC2 | 0 | 5 | 7 | 4-20 mA AI | 5069-IF8
73 | CV-1 |  |  |  | PHASE 1 / 2 COMPRESSED AIR JUMPER VALVE COMMAND |  | INTSL | PROD-UTIL-PLC2 | 0 | 6 | 0 | 4-20 mA AO | 5069-OF8
74 | CV-2 |  |  |  | PHASE 1 / 2 HIGH PRESSURE HOT WATER SUPPLY JUMPER VALVE COMMAND |  | INTSL | PROD-UTIL-PLC2 | 0 | 6 | 1 | 4-20 mA AO | 5069-OF8
75 | CV-3 |  |  |  | PHASE 1 / 2 PROCESS HOT WATER SUPPLY JUMPER VALVE COMMAND |  | INTSL | PROD-UTIL-PLC2 | 0 | 6 | 2 | 4-20 mA AO | 5069-OF8
76 | CV-5 |  |  |  | PHASE 1 / 2 PROCESS HOT WATER RETURN JUMPER VALVE COMMAND |  | INTSL | PROD-UTIL-PLC2 | 0 | 6 | 3 | 4-20 mA AO | 5069-OF8
77 | CV-7 |  |  |  | PHASE 1 / 2 HIGH PRESSURE HOT WATER RETURN JUMPER VALVE COMMAND |  | INTSL | PROD-UTIL-PLC2 | 0 | 6 | 4 | 4-20 mA AO | 5069-OF8
78 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 6 | 5 | 4-20 mA AO | 5069-OF8
79 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 6 | 6 | 4-20 mA AO | 5069-OF8
80 |  |  |  |  | SPARE |  |  | PROD-UTIL-PLC2 | 0 | 6 | 7 | 4-20 mA AO | 5069-OF8
[13 empty] | --------- | ------------ | DEVICE INSTALLED | DEVICE TAGGED | CA INSTALLED | RACEWAYS COMPLETE | WIRE PULLED | WIRE TERMED | WIRE TAGGED | POINT TO POINT | IO CHECK | IO GOOD
[13 empty] | COMPLETED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | % COMPLETE |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0%
[13 empty] | % REMAINING |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 100%
PROCESSING
[13 empty] | COMPLETED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | % COMPLETE |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0%
[13 empty] | % REMAINING |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 100%
CHILLING
[13 empty] | COMPLETED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | % COMPLETE |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0%
[13 empty] | % REMAINING |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 100%
INTERSTITIAL
[13 empty] | COMPLETED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | % COMPLETE |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0%
[13 empty] | % REMAINING |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 100%
HEAT EXCHANGER / LACTIC ACID
[13 empty] | COMPLETED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | % COMPLETE |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0%
[13 empty] | % REMAINING |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 100%
MCC
[13 empty] | COMPLETED |  | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | TOTAL |  | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | % COMPLETE |  | #DIV/0! | #DIV/0! | N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0%
[13 empty] | % REMAINING |  | #DIV/0! | #DIV/0! | N/A | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 100%

## MCC Info
MCC | BUCKET | EQUIP ID | DESCRIPTION | BUCKET TYPE | MOTOR HP | STARTER HP RATING | VFD AMP RATING | STARTER SIZE | SF | CB TRIP | CB FRAME | FUSE TRIP | CABLE | NOTES | RACEWAYS COMPLETE | FEEDER PULLED | FEEDER TERMED | MOTOR BUMPED | AUX POINT TO POINT | AUX I/O CHECK | COMMS PULLED | COMMS TERMED | COMMS TESTED | COMMS TAGGED | COMMS CONFIG | COMMS GOOD | REVIT FAMILY | FAMILY TYPE | GRAPHICS | SECTION | START UNIT | START INDEX | SIZE | UNITS USED | END INDEX
RL7-6MCC01 | 01A | MAIN | INCOMING MCB | MAIN |  |  |  |  | 3.5 | 1200 | 1200 | [15 empty] | Oneline_MCC | MCC_MB-Bus3 | Power-Meter | 1 | A | 1 | 42 | 7 | 7
RL7-6MCC01 | 01H | RL7-MCC1-PM | POWERMONITOR 5000 W/ ETHERNET | PM |  |  |  |  | 1.5 | N/A | N/A | 0.75 | [14 empty] | Oneline_MCC | MCC_MB-Bus3 | Power-Meter | 1 | H | 8 | 18 | 3 | 10
RL7-6MCC01 | 01L | SPARE | SZ1 FVNR - 1.5HP | FVNR |  | 1.5 |  |  | 1 | 7 | 125 | [15 empty] | Oneline_Motor | Motor_FVNR | Motor w/ Disc | 1 | L | 11 | 12 | 2 | 12
RL7-6MCC01 | 2A | RL7-MCC1-2A.SW1 RL7-MCC1-2A.SW2 | ETHERNET SWITCH (10-PORT) ETHERNET SWITCH (20-PORT) | ENET_30 |  |  |  |  | 1 | [17 empty] | Oneline_Ensw | Switch_30-Port |  | 2 | A | 1 | 12 | 2 | 2
RL7-6MCC01 | 02C | RL7-MCC1-2C.PS1 | ETHERNET SWITCH POWER SUPPLY | ENET_PS |  |  |  |  | 1 | [17 empty] | Oneline_Ensw_Power_Supply | PS_2Ckt-External-Power |  | 2 | C | 3 | 12 | 2 | 4
RL7-6MCC01 | 02E | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 2 | E | 5 | 6 | 1 | 5
RL7-6MCC01 | 02F | SPARE | SZ1 FVNR - 7.5HP | FVNR |  | 7.5 |  |  | 1 | 30 | 125 | [15 empty] | Oneline_Motor | Motor_FVNR | Motor w/ Disc | 2 | F | 6 | 12 | 2 | 7
RL7-6MCC01 | 02H | SPARE | VFD - 10HP | VFD_PF755 |  | 10 | 14 |  | 2.5 | 30 | 125 | 25 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 2 | H | 8 | 30 | 5 | 12
RL7-6MCC01 | 03A | SPARE | VFD - 60HP | VFD_PF755 |  | 60 | 77 |  | 6 | 200 | 250 | 125 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 3 | A | 1 | 72 | 12 | 12
RL7-6MCC01 | 04A | RL7-GRR-101.M1 | FINISH GRINDER | VFD_PF755 | 215 | 250 | 302 |  | 6 | 600 | 800 | 500 | 3/C 400 MCM VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 4 | A | 1 | 72 | 12 | 12
RL7-6MCC01 | 05A | SPARE | VFD - 10HP | VFD_PF755 |  | 10 | 14 |  | 2.5 | 30 | 125 | 25 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 5 | A | 1 | 30 | 5 | 5
RL7-6MCC01 | 05F | SPARE | VFD - 25HP | VFD_PF755 |  | 25 | 34 |  | 3.5 | 60 | 125 | 60 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 5 | F | 6 | 42 | 7 | 12
RL7-6MCC01 | 06A | RL7-CNV-112.M1 | SURGE BIN TAKE AWAY CONVEYOR | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 6 | A | 1 | 24 | 4 | 4
RL7-6MCC01 | 06E | RL7-CNV-115.M1 | INCLINE BELT CONVEYOR 2 | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 6 | E | 5 | 24 | 4 | 8
RL7-6MCC01 | 06J | RL7-CNV-116.M1 | ROTOCLAW BELT CONVEYOR | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 6 | J | 9 | 24 | 4 | 12
RL7-6MCC01 | 07A | RL7-CNV-113.M1 | INCLINE BELT CONVEYOR 1 | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 7 | A | 1 | 24 | 4 | 4
RL7-6MCC01 | 07E | SPARE | VFD - 2HP | VFD_PF755 |  | 2 | 3.4 |  | 2 | 15 | 125 | 6 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 7 | E | 5 | 24 | 4 | 8
RL7-6MCC01 | 07J | RL7-CNV-111.M1 | SURGE BIN SUPPLY CONVEYOR | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 7 | J | 9 | 24 | 4 | 12
RL7-6MCC01 | 08A | RL7-BIN-101.M1 | SURGE BIN 1 UPPER AGITATOR | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 8 | A | 1 | 30 | 5 | 5
RL7-6MCC01 | 08F | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 8 | F | 6 | 12 | 2 | 7
RL7-6MCC01 | 08H | RL7-BIN-101.M2 | SURGE BIN 1 AUGER | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 8 | H | 8 | 30 | 5 | 12
RL7-6MCC01 | 09A | RL7-BIN-102.M1 | SURGE BIN 2 UPPER AGITATOR | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 9 | A | 1 | 30 | 5 | 5
RL7-6MCC01 | 09F | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 9 | F | 6 | 12 | 2 | 7
RL7-6MCC01 | 09H | RL7-BIN-102.M2 | SURGE BIN 2 AUGER | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 9 | H | 8 | 30 | 5 | 12
RL7-6MCC01 | 10A | RL7-BIN-103.M1 | SURGE BIN 3 UPPER AGITATOR | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 10 | A | 1 | 30 | 5 | 5
RL7-6MCC01 | 10F | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 10 | F | 6 | 12 | 2 | 7
RL7-6MCC01 | 10H | RL7-BIN-103.M2 | SURGE BIN 3 AUGER | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 10 | H | 8 | 30 | 5 | 12
RL7-6MCC01 | 11A | RL7-BIN-104.M1 | SURGE BIN 4 UPPER AGITATOR | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 11 | A | 1 | 30 | 5 | 5
RL7-6MCC01 | 11F | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 11 | F | 6 | 12 | 2 | 7
RL7-6MCC01 | 11H | RL7-BIN-104.M2 | SURGE BIN 4 AUGER | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 11 | H | 8 | 30 | 5 | 12
RL7-6MCC01 | 12A | RL7-CNV-110.M1 | METAL DETECTOR CONVEYOR | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 12 | A | 1 | 24 | 4 | 4
RL7-6MCC01 | 12E | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 12 | E | 5 | 6 | 1 | 5
RL7-6MCC01 | 12F | RL7-CNV-109.M1 | INCLINE AUGER CONVEYOR | VFD_PF755 | 25 | 25 | 34 |  | 3.5 | 60 | 125 | 60 | 3/C #8 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 12 | F | 6 | 42 | 7 | 12
RL7-6MCC01 | 13A | RL7-CNV-114.M2 | INCLINE PIVOT AUGER 1 HYDRAULIC PUMP | FVNR | 1.5 | 1.5 |  | 1 | 1 | 7 | 125 |  | 3/C #12 W/ GND | [13 empty] | Oneline_Motor | Motor_FVNR | Motor w/ Disc | 13 | A | 1 | 12 | 2 | 2
RL7-6MCC01 | 13C | RL7-CNV-114.M1 | INCLINE PIVOT AUGER 1 | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 13 | C | 3 | 30 | 5 | 7
RL7-6MCC01 | 13H | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 13 | H | 8 | 6 | 1 | 8
RL7-6MCC01 | 13J | RL7-CNV-114.M3 | INCLINE PIVOT AUGER 1 SLIDE TRACK | VFD_PF755 | 0.75 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 13 | J | 9 | 24 | 4 | 12
RL7-6MCC01 | 14A | RL7-MCC1-14A.SW1 RL7-MCC1-14A.SW2 | ETHERNET SWITCH (10-PORT) ETHERNET SWITCH (20-PORT) | ENET_30 |  |  |  |  | 1 | [17 empty] | Oneline_Ensw | Switch_30-Port |  | 14 | A | 1 | 12 | 2 | 2
RL7-6MCC01 | 14C | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 14 | C | 3 | 12 | 2 | 4
RL7-6MCC01 | 14E | RL7-AGC-101.M1 | FRESH AUGER CART 1 - AUGER 1 | VFD_PF755 | 5 | 5 | 8 |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 14 | E | 5 | 24 | 4 | 8
RL7-6MCC01 | 14J | RL7-AGC-101.M2 | FRESH AUGER CART 1 - AUGER 2 | VFD_PF755 | 5 | 5 | 8 |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 14 | J | 9 | 24 | 4 | 12
RL7-6MCC01 | 15A | RL7-PMP-101.M1 | FRESH AUGER CART 1 - PUMP | VFD_PF755 | 20 | 20 | 27 |  | 3 | 60 | 125 | 45 | 3/C #10 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 15 | A | 1 | 36 | 6 | 6
RL7-6MCC01 | 15G | RL7-PMP-102.M1 | FRESH AUGER CART 2 - PUMP | VFD_PF755 | 20 | 20 | 27 |  | 3 | 60 | 125 | 45 | 3/C #10 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 15 | G | 7 | 36 | 6 | 12
RL7-6MCC01 | 16A | RL7-MLT-104.M1 | FRESH AUGER CART 1 - COMBO DUMPER | FVNR | 7.5 | 7.5 |  | 1 | 1 | 30 | 125 |  | 3/C #12 W/ GND | [13 empty] | Oneline_Motor | Motor_FVNR | Motor w/ Disc | 16 | A | 1 | 12 | 2 | 2
RL7-6MCC01 | 16C | RL7-MLT-105.M1 | FRESH AUGER CART 2 - COMBO DUMPER | FVNR | 7.5 | 7.5 |  | 1 | 1 | 30 | 125 |  | 3/C #12 W/ GND | [13 empty] | Oneline_Motor | Motor_FVNR | Motor w/ Disc | 16 | C | 3 | 12 | 2 | 4
RL7-6MCC01 | 16E | RL7-AGC-102.M1 | FRESH AUGER CART 2 - AUGER 1 | VFD_PF755 | 5 | 5 | 8 |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 16 | E | 5 | 24 | 4 | 8
RL7-6MCC01 | 16J | RL7-AGC-102.M2 | FRESH AUGER CART 2 - AUGER 2 | VFD_PF755 | 5 | 5 | 8 |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 16 | J | 9 | 24 | 4 | 12
RL7-6MCC01 | 17A | RL7-GRR-103.M1 | FROZEN BLOCK CRUSHER | VFD_PF755 | 50 | 50 | 65 |  | 6 | 125 | 125 | 100 | 3/C #4 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 17 | A | 1 | 72 | 12 | 12
RL7-6MCC01 | 18A | RL7-GRR-103.M2 | FROZEN BLOCK CRUSHER | VFD_PF755 | 50 | 50 | 65 |  | 6 | 125 | 125 | 100 | 3/C #4 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 18 | A | 1 | 72 | 12 | 12
RL7-6MCC02 | 01A | MAIN | INCOMING MCB | MAIN |  |  |  |  | 3.5 | 1200 | 1200 | [15 empty] | Oneline_MCC | MCC_MB-Bus4 | Power-Meter | 1 | A | 1 | 42 | 7 | 7
RL7-6MCC02 | 01H | RL7-MCC2-PM | POWERMONITOR 5000 W/ ETHERNET | PM |  |  |  |  | 1.5 |  |  | 0.75 | [14 empty] | Oneline_MCC | MCC_MB-Bus4 | Power-Meter | 1 | H | 8 | 18 | 3 | 10
RL7-6MCC02 | 01L | RL7-DRM-101.M1 | BREDDO DUMPER | FVNR | 2 | 2 |  | 1 | 1 | 7 | 125 |  | 3/C #12 W/ GND | [13 empty] | Oneline_Motor | Motor_FVNR | Motor w/ Disc | 1 | L | 11 | 12 | 2 | 12
RL7-6MCC02 | 02A | RL7-MCC2-2A.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [17 empty] | Oneline_Ensw | Switch_20-Port |  | 2 | A | 1 | 12 | 2 | 2
RL7-6MCC02 | 02C | RL7-MCC2-2C.PS1 | ETHERNET SWITCH POWER SUPPLY | ENET_PS |  |  | 14 |  | 1 | [17 empty] | Oneline_Ensw_Power_Supply | PS_2Ckt-External-Power |  | 2 | C | 3 | 12 | 2 | 4
RL7-6MCC02 | 02E | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 2 | E | 5 | 6 | 1 | 5
RL7-6MCC02 | 02F | SPARE | VFD - 25HP | VFD_PF755 | 25 | 25 | 34 |  | 3.5 | 60 | 125 | 60 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 2 | F | 6 | 42 | 7 | 12
RL7-6MCC02 | 03A | RL7-CKR-101.M1 | COOKER 1 - AGITATOR 1 (LEFT) | VFD_PF755 | 25 | 25 | 34 |  | 3.5 | 60 | 125 | 60 | 3/C #8 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 3 | A | 1 | 42 | 7 | 7
RL7-6MCC02 | 03H | SPARE | VFD - 2HP | VFD_PF755 |  | 2 | 3.4 |  | 2 | 15 | 125 | 6 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 3 | H | 8 | 24 | 4 | 11
RL7-6MCC02 | 03M | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 3 | M | 12 | 6 | 1 | 12
RL7-6MCC02 | 04A | RL7-CKR-101.M2 | COOKER 1 - AGITATOR 2 (RIGHT) | VFD_PF755 | 25 | 25 | 34 |  | 3.5 | 60 | 125 | 60 | 3/C #8 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 4 | A | 1 | 42 | 7 | 7
RL7-6MCC02 | 04H | SPARE | VFD - 2HP | VFD_PF755 |  | 2 | 3.4 |  | 2 | 15 | 125 | 6 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 4 | H | 8 | 24 | 4 | 11
RL7-6MCC02 | 04M | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 4 | M | 12 | 6 | 1 | 12
RL7-6MCC02 | 05A | RL7-CKR-102.M1 | COOKER 2 - AGITATOR 1 (LEFT) | VFD_PF755 | 25 | 25 | 34 |  | 3.5 | 60 | 125 | 60 | 3/C #8 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 5 | A | 1 | 42 | 7 | 7
RL7-6MCC02 | 05H | SPARE | VFD - 2HP | VFD_PF755 |  | 2 | 3.4 |  | 2 | 15 | 125 | 6 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 5 | H | 8 | 24 | 4 | 11
RL7-6MCC02 | 05M | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 5 | M | 12 | 6 | 1 | 12
RL7-6MCC02 | 06A | RL7-SKD-101.M1 | BREDDO MIXER | VFD_PF755 | 75 | 75 | 96 |  | 6 | 250 | 250 | 175 | 3/C #1 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 6 | A | 1 | 72 | 12 | 12
RL7-6MCC02 | 07A | RL7-CKR-102.M2 | COOKER 2 - AGITATOR 2 (RIGHT) | VFD_PF755 | 25 | 25 | 34 |  | 3.5 | 60 | 125 | 60 | 3/C #8 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 7 | A | 1 | 42 | 7 | 7
RL7-6MCC02 | 07H | RL7-PRM-101.M1 | PRE-MIXER DISCHARGE SCREW | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | FED THRU JIC2A | [12 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 7 | H | 8 | 30 | 5 | 12
RL7-6MCC02 | 08A | RL7-SKD-101.M2 | BREDDO MIXER AGITATOR | VFD_PF755 | 5 | 5 | 8 |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 8 | A | 1 | 24 | 4 | 4
RL7-6MCC02 | 08E | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 8 | E | 5 | 12 | 2 | 6
RL7-6MCC02 | 08G | RL7-PMP-104.M1 | COOKER 1 - PUMP | VFD_PF755 | 20 | 20 | 27 |  | 3 | 60 | 125 | 45 | 3/C #10 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 8 | G | 7 | 36 | 6 | 12
RL7-6MCC02 | 09A | RL7-FAN-103.M1 | COOKER 1 HOOD EXHAUST FAN | VFD_PF755 | 5 | 5 | 8 |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 9 | A | 1 | 24 | 4 | 4
RL7-6MCC02 | 09E | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 9 | E | 5 | 12 | 2 | 6
RL7-6MCC02 | 09G | RL7-PMP-105.M1 | COOKER 2 - PUMP | VFD_PF755 | 20 | 20 | 27 |  | 3 | 60 | 125 | 45 | 3/C #10 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 9 | G | 7 | 36 | 6 | 12
RL7-6MCC02 | 10A | RL7-FAN-104.M1 | COOKER 2 HOOD EXHAUST FAN | VFD_PF755 | 5 | 5 | 8 |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 10 | A | 1 | 24 | 4 | 4
RL7-6MCC02 | 10E | RL7-PMP-103.M1 | BREDDO MIXER PUMP | VFD_PF755 | 20 | 20 | 27 |  | 3 | 60 | 125 | 45 | 3/C #10 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 10 | E | 5 | 36 | 6 | 10
RL7-6MCC02 | 10L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 10 | L | 11 | 12 | 2 | 12
RL7-6MCC02 | 11A | SPACE | 18" SPACE | SPACE |  |  |  |  | 1.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 11 | A | 1 | 18 | 3 | 3
RL7-6MCC02 | 11D | RL7-SKD-102.M1 | LACTIC ACID SKID PUMP | VFD_PF755 | 2 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 11 | D | 4 | 24 | 4 | 7
RL7-6MCC02 | 11H | RL7-PMP-108.M1 | HOT WATER JACKET PUMP | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 11 | H | 8 | 30 | 5 | 12
RL7-6MCC02 | 12A | RL7-MCC2-12A.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [17 empty] | Oneline_Ensw | Switch_20-Port |  | 12 | A | 1 | 12 | 2 | 2
RL7-6MCC02 | 12C | SPARE | SZ1 FVNR - 5HP | FVNR |  | 5 |  | 1 | 1 | 15 | 125 |  | 3/C #12 W/ GND | [13 empty] | Oneline_Motor | Motor_FVNR | Motor w/ Disc | 12 | C | 3 | 12 | 2 | 4
RL7-6MCC02 | 12E | RL7-FAN-101.M1 | COOKER 1 - EXHAUST FAN | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 12 | E | 5 | 24 | 4 | 8
RL7-6MCC02 | 12J | RL7-FAN-102.M1 | COOKER 2 - EXHAUST FAN | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 12 | J | 9 | 24 | 4 | 12
RL7-6MCC02 | 13A | RL7-PRM-101.M2 RL7-PRM-101.M3 | PRE-MIXER AGITATORS | VFD_PF755 | (2) 30 | 75 | 96 |  | 6 | 250 | 250 | 175 | 3/C #6 VFD CABLE | SHARED VFD - FED THRU JIC2A | [12 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 13 | A | 1 | 72 | 12 | 12
RL7-6MCC02 | 14A | RL7-PMP-106.M1 | PRE-MIXER PUMP | VFD_PF755 |  | 75 | 96 |  | 6 | 250 | 250 | 175 | 3/C #1 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 14 | A | 1 | 72 | 12 | 12
RL7-6MCC02 | 15A | SPACE | 6" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 15 | A | 1 | 12 | 2 | 2
RL7-6MCC02 | 15C | RL7-MLT-107.M1 | COOKER 1 - COLUMN DUMPER | FVR | 1.5 | 1.5 |  | 1 | 1.5 | 7 | 125 |  | 3/C #12 W/ GND | FED THRU COOKER 1 JIC4A | [12 empty] | Oneline_Motor | Motor_FVR | Motor w/ Disc | 15 | C | 3 | 18 | 3 | 5
RL7-6MCC02 | 15F | RL7-MLT-108.M1 | COOKER 2 - COLUMN DUMPER | FVR | 1.5 | 1.5 |  | 1 | 1.5 | 7 | 125 |  | 3/C #12 W/ GND | FED THRU COOKER 2 JIC3A | [12 empty] | Oneline_Motor | Motor_FVR | Motor w/ Disc | 15 | F | 6 | 18 | 3 | 8
RL7-6MCC02 | 15J | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 15 | J | 9 | 12 | 2 | 10
RL7-6MCC02 | 15L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 15 | L | 11 | 12 | 2 | 12
RL7-6MCC02 | 16A | RL7-MCC2-16A.SW1 RL7-MCC2-16A.SW2 | ETHERNET SWITCHES (10P & 20P) | ENET_30 |  |  |  |  | 1 | [17 empty] | Oneline_Ensw | Switch_20-Port |  | 16 | A | 1 | 12 | 2 | 2
RL7-6MCC02 | 16C | SPARE | VFD - 5HP | VFD_PF755 |  | 5 | 8 |  | 2 | 20 | 125 | 12 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 16 | C | 3 | 24 | 4 | 6
RL7-6MCC02 | 16G | RL7-MLT-106.M1 | PRE-MIXER COLUMN DUMPER | FVR | 1.5 | 1.5 |  | 1 | 1.5 | 7 | 125 |  | 3/C #12 W/ GND | [13 empty] | Oneline_Motor | Motor_FVR | Motor w/ Disc | 16 | G | 7 | 18 | 3 | 9
RL7-6MCC02 | 16K | SPACE | 18" SPACE | SPACE |  |  |  |  | 1.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 16 | K | 10 | 18 | 3 | 12
RL7-6MCC02 | 17A | SPARE | SZ1 FVNR - 1.5HP | FVNR |  | 1.5 |  |  | 1 | 7 | 125 | [15 empty] | Oneline_Motor | Motor_FVNR | Motor w/ Disc | 17 | A | 1 | 12 | 2 | 2
RL7-6MCC02 | 17C | SPARE | VFD - 2HP | VFD_PF755 |  | 2 | 3.4 |  | 2 | 15 | 125 | 6 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 17 | C | 3 | 24 | 4 | 6
RL7-6MCC02 | 17G | SPARE | VFD - 10HP | VFD_PF755 |  | 10 | 14 |  | 2.5 | 30 | 125 | 25 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 17 | G | 7 | 30 | 5 | 11
RL7-6MCC02 | 17M | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 17 | M | 12 | 6 | 1 | 12
RL7-6MCC02 | 18A | RL7-CNV-106.M2 | INCLINE PIVOT AUGER 2 HYDRAULIC PUMP | FVNR | 1.5 | 1.5 |  | 1 | 1 | 7 | 125 |  | 3/C #12 W/ GND | [13 empty] | Oneline_Motor | Motor_FVNR | Motor w/ Disc | 18 | A | 1 | 12 | 2 | 2
RL7-6MCC02 | 18C | RL7-CNV-106.M3 | INCLINE PIVOT AUGER 2 SLIDE TRACK | VFD_PF755 | 0.75 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 18 | C | 3 | 24 | 4 | 6
RL7-6MCC02 | 18G | RL7-CNV-106.M1 | INCLINE PIVOT AUGER 2 | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 18 | G | 7 | 30 | 5 | 11
RL7-6MCC02 | 18M | SPACE | 6" SPACE | SPACE |  |  | 14 |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 18 | M | 12 | 6 | 1 | 12
RL7-6MCC02 | 19A | RL7-MCC2-19A.PS1 | ETHERNET SWITCH POWER SUPPLY | ENET_PS |  |  | 14 |  | 1 | [17 empty] | Oneline_Ensw_Power_Supply | PS_2Ckt-External-Power |  | 19 | A | 1 | 12 | 2 | 2
RL7-6MCC02 | 19C | SPARE | VFD - 10HP | VFD_PF755 |  | 10 | 14 |  | 2.5 | 30 | 125 | 25 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 19 | C | 3 | 30 | 5 | 7
RL7-6MCC02 | 19H | SPARE | VFD - 10HP | VFD_PF755 |  | 10 | 14 |  | 2.5 | 30 | 125 | 25 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 19 | H | 8 | 30 | 5 | 12
RL7-6MCC03 | 01A | MAIN | INCOMING MCB | MAIN |  |  |  |  | 3.5 | 1200 | 1200 | [15 empty] | Oneline_MCC | MCC_MB-Bus3 | Power-Meter | 1 | A | 1 | 42 | 7 | 7
RL7-6MCC03 | 01H | RL7-MCC3-PM | POWERMONITOR 5000 W/ ETHERNET | PM |  |  |  |  | 1.5 |  |  | 0.75 | [14 empty] | Oneline_MCC | MCC_MB-Bus3 | Power-Meter | 1 | H | 8 | 18 | 3 | 10
RL7-6MCC03 | 01L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 1 | L | 11 | 12 | 2 | 12
RL7-6MCC03 | 02A | RL7-MCC3-2A.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [17 empty] | Oneline_Ensw | Switch_20-Port |  | 2 | A | 1 | 12 | 2 | 2
RL7-6MCC03 | 02C | RL7-MCC3-2C.PS1 | ETHERNET SWITCH POWER SUPPLY | ENET_PS |  |  |  |  | 1 | [17 empty] | Oneline_Ensw_Power_Supply | PS_2Ckt-External-Power |  | 2 | C | 3 | 12 | 2 | 4
RL7-6MCC03 | 02E | SPARE | VFD - 1HP | SPARE |  | 1 | 2.1 |  | 2 | [17 empty] | Oneline_Ensw | Switch_20-Port |  | 2 | E | 5 | 24 | 4 | 8
RL7-6MCC03 | 02J | SPARE | VFD - 5HP | SPARE |  | 5 | 8 |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Ensw | Switch_20-Port |  | 2 | J | 9 | 24 | 4 | 12
RL7-6MCC03 | 03A | RL7-CNV-201.M1 | ROLL FILLER DISCHARGE CONVEYOR | VFD_PF755 | 0.5 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | NEEDS MELTRIC | [12 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 3 | A | 1 | 24 | 4 | 4
RL7-6MCC03 | 03E | RL7-CNV-203.M1 | SERPENTINE INFEED CONVEYOR 2 | VFD_PF755 | 0.5 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 3 | E | 5 | 24 | 4 | 8
RL7-6MCC03 | 03J | RL7-CNV-204.M1 | SERPENTINE INFEED CONVEYOR 3 | VFD_PF755 | 0.5 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 3 | J | 9 | 24 | 4 | 12
RL7-6MCC03 | 04A | RL7-AGC-201.M1 | DISCHARGE AUGER CART - LEVELING RIBBON | VFD_PF755 | 5 | 5 | 8 |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 4 | A | 1 | 24 | 4 | 4
RL7-6MCC03 | 04E | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 4 | E | 5 | 6 | 1 | 5
RL7-6MCC03 | 04F | RL7-SKD-201.M1 | CLEAN ASSIST FOAM PUMP | VFD_PF755 | 10 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 4 | F | 6 | 30 | 5 | 10
RL7-6MCC03 | 04L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 4 | L | 11 | 12 | 2 | 12
RL7-6MCC03 | 05A | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 5 | A | 1 | 12 | 2 | 2
RL7-6MCC03 | 05C | RL7-PMP-201.M1 | DISCHARGE AUGER CART PUMP | VFD_PF755 | 7.5 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 5 | C | 3 | 30 | 5 | 7
RL7-6MCC03 | 05H | RL7-AGC-201.M2 | DISCHARGE AUGER CART AUGER | VFD_PF755 | 7.5 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 5 | H | 8 | 30 | 5 | 12
RL7-6MCC03 | 06A | RL7-CNV-205.M1 | SERPENTINE DISCHARGE CONVEYOR 1 | VFD_PF755 | 0.5 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 6 | A | 1 | 24 | 4 | 4
RL7-6MCC03 | 06E | RL7-CNV-202.M1 | SERPENTINE INFEED CONVEYOR 1 | VFD_PF755 | 0.5 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 6 | E | 5 | 24 | 4 | 8
RL7-6MCC03 | 06J | RL7-CNV-403.M1 | METERING CONVEYOR 2 | VFD_PF755 | 0.5 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 6 | J | 9 | 24 | 4 | 12
RL7-6MCC03 | 07A | RL7-CHR-201.M1 | SERPENTINE MAIN DRIVE | VFD_PF755 | 7.5 | 10 | 14 |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 7 | A | 1 | 30 | 5 | 5
RL7-6MCC03 | 07F | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [17 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 7 | F | 6 | 6 | 1 | 6
RL7-6MCC03 | 07G | SPARE | VFD - 20HP | VFD_PF755 |  | 20 | 27 |  | 3 | 60 | 125 | 45 | [14 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 7 | G | 7 | 36 | 6 | 12
RL7-6MCC03 | 08A | RL7-PMP-203.M1 | SERPENTINE HEX 1 PUMP | VFD_PF755 | 60 | 60 | 77 |  | 6 | 200 | 250 | 125 | 3/C #2 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 8 | A | 1 | 72 | 12 | 12
RL7-6MCC03 | 09A | RL7-PMP-204.M1 | SERPENTINE RECIRC 1 PUMP | VFD_PF755 | 60 | 60 | 77 |  | 6 | 200 | 250 | 125 | 3/C #2 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 9 | A | 1 | 72 | 12 | 12
RL7-6MCC03 | 10A | RL7-PMP-205.M1 | SERPENTINE HEX 2 PUMP | VFD_PF755 | 60 | 60 | 77 |  | 6 | 200 | 250 | 125 | 3/C #2 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 10 | A | 1 | 72 | 12 | 12
RL7-6MCC03 | 11A | RL7-PMP-206.M1 | SERPENTINE RECIRC 2 PUMP | VFD_PF755 | 60 | 60 | 77 |  | 6 | 200 | 250 | 125 | 3/C #2 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 11 | A | 1 | 72 | 12 | 12
RL7-6MCC03 | 12A | RL7-PMP-207.M1 | SERPENTINE HEX 3 PUMP | VFD_PF755 | 60 | 60 | 77 |  | 6 | 200 | 250 | 125 | 3/C #2 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 12 | A | 1 | 72 | 12 | 12
RL7-6MCC03 | 13A | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | 60 | 125 | 45 | [14 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 13 | A | 1 | 12 | 2 | 2
RL7-6MCC03 | 13C | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | 60 | 125 | 45 | [14 empty] | Oneline_Feeder_Panel | Feeder_Space |  | 13 | C | 3 | 12 | 2 | 4
RL7-6MCC03 | 13E | RL7-FTR-205.M1 | SERPENTINE ZONE 2A FILTER | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 13 | E | 5 | 24 | 4 | 8
RL7-6MCC03 | 13J | RL7-FTR-207.M1 | SERPENTINE ZONE 2B FILTER | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 13 | J | 9 | 24 | 4 | 12
RL7-6MCC03 | 14A | SPARE | VFD - 1HP | SPARE |  | 1 | 2.1 |  | 2 | [17 empty] | Oneline_Ensw | Switch_20-Port |  | 14 | A | 1 | 24 | 4 | 4
RL7-6MCC03 | 14E | SPARE | VFD - 1HP | SPARE |  | 1 | 2.1 |  | 2 | [17 empty] | Oneline_Ensw | Switch_20-Port |  | 14 | E | 5 | 24 | 4 | 8
RL7-6MCC03 | 14J | SPARE | VFD - 1HP | SPARE |  | 1 | 2.1 |  | 2 | [17 empty] | Oneline_Ensw | Switch_20-Port |  | 14 | J | 9 | 24 | 4 | 12
RL7-6MCC03 | 15A | RL7-CNV-402.M1 | METERING CONVEYOR 1 | VFD_PF755 | 0.5 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 15 | A | 1 | 24 | 4 | 4
RL7-6MCC03 | 15E | RL7-CNV-401.M1 | INSPECTION CONVEYOR | VFD_PF755 | 0.5 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 15 | E | 5 | 24 | 4 | 8
RL7-6MCC03 | 15J | RL7-CNV-206.M1 | SERPENTINE DISCHARGE CONVEYOR 2 | VFD_PF755 | 0.5 | 1 | 2.1 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 15 | J | 9 | 24 | 4 | 12
RL7-6MCC03 | 16A | RL7-MCC3-16A.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [17 empty] | Oneline_Ensw | Switch_20-Port |  | 16 | A | 1 | 12 | 2 | 2
RL7-6MCC03 | 16C | RL7-CNV-404.M1 | CASE PACKER INFEED CONVEYOR | VFD_PF755 | 1 | 2 | 3.4 |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 16 | C | 3 | 24 | 4 | 6
RL7-6MCC03 | 16G | RL7-FAN-201.M1 | AIR KNIFE BLOWER | VFD_PF755 | 15 | 15 | 22 |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [13 empty] | Oneline_Motor | Motor_VFD-w-Fuse | Motor w/ Disc | 16 | G | 7 | 36 | 6 | 12
RM6-6MCC01 | 01A | MAIN | INCOMING MCB | MAIN |  |  |  |  | 3.5 | 1000 | 1200 | N/A | [17 empty] | 1 | A | 1 | 42 | 7 | 7
RM6-6MCC01 | 01H | RM6-MCC1-PM | POWERMONITOR 5000 W/ ETHERNET | PM |  |  |  |  | 1.5 | N/A | N/A | 0.75 | [17 empty] | 1 | H | 8 | 18 | 3 | 10
RM6-6MCC01 | 01L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 1 | L | 11 | 12 | 2 | 12
RM6-6MCC01 | 02A | RM6-CNV-101.M1 | INCLINE AUGER CONVEYOR | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | 70 | 3/C #8 VFD CABLE | [16 empty] | 2 | A | 1 | 42 | 7 | 7
RM6-6MCC01 | 02H | RM6-MCC1-02H.PS1 | ETHERNET SWITCH POWER SUPPLY | ENET_PS |  |  |  |  | 1.5 | 15 | 125 | [18 empty] | 2 | H | 8 | 18 | 3 | 10
RM6-6MCC01 | 02L | RM6-MCC1-02L.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [20 empty] | 2 | L | 11 | 12 | 2 | 12
RM6-6MCC01 | 03A | RM6-GRR-105.M1 | STEAM COOKER 1 DE-CLUMPER | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 3 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 03E | RM6-BIN-101C.M2 | SURGE BIN 3 AUGER | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 3 | E | 5 | 36 | 6 | 10
RM6-6MCC01 | 03L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 3 | L | 11 | 12 | 2 | 12
RM6-6MCC01 | 04A | RM6-CKR-101.M1 | STEAM COOKER 1 STEAM BELT 1 | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 4 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 04E | RM6-WWL-101.M1 RM6-SHR-101.M1 | STEAM COOKER 1 WATERWHEEL/SPREADER MOTOR 1 | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 4 | E | 5 | 24 | 4 | 8
RM6-6MCC01 | 04J | RM6-CKR-101.M2 | STEAM COOKER 1 STEAM BELT 2 | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 4 | J | 9 | 24 | 4 | 12
RM6-6MCC01 | 05A | RM6-FAN-101.M1 | STEAM COOKER 1 EXHAUST FAN 1 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 40 | 3/C #12 VFD CABLE | [16 empty] | 5 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 05E | RM6-FAN-102.M1 | STEAM COOKER 1 EXHAUST FAN 2 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 40 | 3/C #12 VFD CABLE | [16 empty] | 5 | E | 5 | 24 | 4 | 8
RM6-6MCC01 | 05J | RM6-FAN-103.M1 | STEAM COOKER 1 EXHAUST FAN 3 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 40 | 3/C #12 VFD CABLE | [16 empty] | 5 | J | 9 | 24 | 4 | 12
RM6-6MCC01 | 06A | RM6-BIN-101B.M2 | SURGE BIN 2 AUGER | VFD | 15 | 15 |  |  | 1 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 6 | A | 1 | 12 | 2 | 2
RM6-6MCC01 | 06C | RM6-CNV-112.M1 | STEAM COOKER 1 DISCHARGE CONVEYOR | VFD | 2 | 2 |  |  | 4 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 6 | C | 3 | 48 | 8 | 10
RM6-6MCC01 | 06L | RM6-MCC1-06L.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [20 empty] | 6 | L | 11 | 12 | 2 | 12
RM6-6MCC01 | 07A | RM6-GRR-106.M1 | STEAM COOKER 2 DE-CLUMPER | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 7 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 07E | RM6-CKR-102.M1 | STEAM COOKER 2 STEAM BELT 1 | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 7 | E | 5 | 24 | 4 | 8
RM6-6MCC01 | 07J | RM6-WWL-102.M1 RM6-SHR-102.M1 | STEAM COOKER 2 WATERWHEEL/SPREADER MOTOR 1 | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 7 | J | 9 | 24 | 4 | 12
RM6-6MCC01 | 08A | RM6-AGC-103.M2 | DUAL AUGER CART 1 AUGER 1 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 20 | 3/C #12 VFD CABLE | [16 empty] | 8 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 08E | RM6-AGC-103.M3 | DUAL AUGER CART 1 AUGER 2 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 20 | 3/C #12 VFD CABLE | [16 empty] | 8 | E | 5 | 24 | 4 | 8
RM6-6MCC01 | 08J | RM6-AGC-104.M2 | DUAL AUGER CART 2 AUGER 1 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 20 | 3/C #12 VFD CABLE | [16 empty] | 8 | J | 9 | 24 | 4 | 12
RM6-6MCC01 | 09A | RM6-CKR-102.M2 | STEAM COOKER 2 STEAM BELT 2 | [5 empty] | 2 | [20 empty] | 9 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 09E | RM6-CNV-115.M1 | STEAM COOKER 2 DISCHARGE CONVEYOR | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 9 | E | 5 | 24 | 4 | 8
RM6-6MCC01 | 09J | RM6-CNV-107.M1 | INCLINED BELT CONVEYOR | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 9 | J | 9 | 24 | 4 | 12
RM6-6MCC01 | 10A | RM6-AGC.103.M4 | DUAL AUGER CART 1 SLIDING TRACK | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 10 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 10E | RM6-AGC-104.M4 | DUAL AUGER CART 2 SLIDING TRACK | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 10 | E | 5 | 24 | 4 | 8
RM6-6MCC01 | 10J | RM6-CNV-108.M3 | INCLINE CONVEYOR SLIDE TRACK | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 10 | J | 9 | 24 | 4 | 12
RM6-6MCC01 | 11A | RM6-GRR-102.M1 | GRINDER | VFD | 150 | 150 |  |  | 6 | 250 | 250 | 300 | 3/C #250 MCM VFD CABLE | [16 empty] | 11 | A | 1 | 72 | 12 | 12
RM6-6MCC01 | 12A | RM6-SLT-201.M2 | SLITTER | VFD | 3 | 5 |  |  | 2 | 15 | 125 | 15 | 3/C #12 VFD CABLE | [16 empty] | 12 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 12E | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 12 | E | 5 | 6 | 1 | 5
RM6-6MCC01 | 12F | RM6-MGR-101.M4 | MIXER GRINDER 1 GRINDER | VFD | 100 | 100 |  |  | 3.5 | 250 | 250 | 225 | 3/C #2/0 VFD CABLE | [16 empty] | 12 | F | 6 | 42 | 7 | 12
RM6-6MCC01 | 13A | RM6-CRT-201.M1 | VINEGAR SUPPLE CART | VFD | 2 | 2 |  |  | 2 |  |  |  | 3/C #12 VFD CABLE | [16 empty] | 13 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 13E | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 13 | E | 5 | 6 | 1 | 5
RM6-6MCC01 | 13F | RM6-MGR-102.M4 | MIXER GRINDER 2 GRINDER | VFD | 100 | 100 |  |  | 3.5 | 250 | 250 | 225 | 3/C #2/0 VFD CABLE | [16 empty] | 13 | F | 6 | 42 | 7 | 12
RM6-6MCC01 | 14A | RM6-BIN-101D.M2 | SURGE BIN 4 AUGER | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 14 | A | 1 | 36 | 6 | 6
RM6-6MCC01 | 14G | SPARE | VFD - 2HP | VFD |  |  |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 14 | G | 7 | 24 | 4 | 10
RM6-6MCC01 | 14L | RM6-MCC1-14L.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [20 empty] | 14 | L | 11 | 12 | 2 | 12
RM6-6MCC01 | 15A | RM6-BIN-101A.M2 | SURGE BIN 1 AUGER | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 15 | A | 1 | 36 | 6 | 6
RM6-6MCC01 | 15G | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 15 | G | 7 | 6 | 1 | 7
RM6-6MCC01 | 15H | RM6-AGC-103.M1 | DUAL AUGER CART 1 LEVELING RIBON | VFD | 7.5 | 10 |  |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [16 empty] | 15 | H | 8 | 30 | 5 | 12
RM6-6MCC01 | 16A | SPARE | VFD - 2HP | VFD |  |  |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 16 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 16E | RM6-CNV-104.M1 | SURGE BIN SUPPLY CONVEYOR | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 16 | E | 5 | 24 | 4 | 8
RM6-6MCC01 | 16J | RM6-CNV-108.M2 | INCLINE CONVEYOR HYDRAULICS | FVNR | 1.5 | 2 |  | 1 | 1 | 7 | 125 |  | 3/C #12 VFD CABLE | [16 empty] | 16 | J | 9 | 12 | 2 | 10
RM6-6MCC01 | 16L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 16 | L | 11 | 12 | 2 | 12
RM6-6MCC01 | 17A | RM6-FAN-104.M1 | STEAM COOKER 2 EXHAUST FAN 1 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 20 | 3/C #12 VFD CABLE | [16 empty] | 17 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 17E | RM6-FAN-105.M1 | STEAM COOKER 2 EXHAUST FAN 2 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 20 | 3/C #12 VFD CABLE | [16 empty] | 17 | E | 5 | 24 | 4 | 8
RM6-6MCC01 | 17J | RM6-FAN-106.M1 | STEAM COOKER 2 EXHAUST FAN 3 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 20 | 3/C #12 VFD CABLE | [16 empty] | 17 | J | 9 | 24 | 4 | 12
RM6-6MCC01 | 18A | RM6-AGC-104.M3 | DUAL AUGER CART 2 AUGER 2 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 20 | 3/C #12 VFD CABLE | [16 empty] | 18 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 18E | RM6-MLT-103.M1 | MIXER GRINDER 1 COLUMN DUMPER | FVR | 1.5 | 2 |  | 1 | 1.5 | 7 | 125 | N/A | 3/C #12 VFD CABLE | [16 empty] | 18 | E | 5 | 18 | 3 | 7
RM6-6MCC01 | 18H | RM6-AGC-104.M1 | DUAL AUGER CART 2 LEVELING RIBON | VFD | 7.5 | 10 |  |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [16 empty] | 18 | H | 8 | 30 | 5 | 12
RM6-6MCC01 | 19A | SPARE | VFD - 5HP | VFD |  |  |  |  | 2 | 20 | 125 | 20 | 3/C #10 VFD CABLE | [16 empty] | 19 | A | 1 | 24 | 4 | 4
RM6-6MCC01 | 19E | RM6_82 | CIP TANK STARTER | FVNR | 40 | 40 |  | 1 | 1.5 | 70 | 125 | 50 | 3/C #6 W/ GND | [16 empty] | 19 | E | 5 | 18 | 3 | 7
RM6-6MCC01 | 19H | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 19 | H | 8 | 6 | 1 | 8
RM6-6MCC01 | 19J | RM6-SLT-201.M1 | SLITTER | VFD | 1 | 2 |  |  | 2 | 15 | 125 | 3 | 3/C #12 VFD CABLE | [16 empty] | 19 | J | 9 | 24 | 4 | 12
RM6-6MCC02 | 01A | MAIN | INCOMING MCB | MAIN |  |  |  |  | 2.5 | [20 empty] | 1 | A | 1 | 30 | 5 | 5
RM6-6MCC02 | 01F | RM6-MCC2-PM | POWERMONITOR 5000 W/ ETHERNET | PM |  |  |  |  | 1.5 | N/A | N/A | 0.75 | [17 empty] | 1 | F | 6 | 18 | 3 | 8
RM6-6MCC02 | 01J | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 1 | J | 9 | 6 | 1 | 9
RM6-6MCC02 | 01K | RM6-MCC2-01K.PS1 | ETHERNET SWITCH POWER SUPPLY | ENET_PS |  |  |  |  | 1.5 | 15 | 125 | [18 empty] | 1 | K | 10 | 18 | 3 | 12
RM6-6MCC02 | 02A | RM6-MGR-101.M3 | MIXER GRINDER 1 DISCHARGE SCREW | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 2 | A | 1 | 36 | 6 | 6
RM6-6MCC02 | 02G | RM6-SKD-101.M1 | VOTATOR PMP-201 COOKER 1 | VFD | 3 | 5 |  |  | 2 | 15 | 125 | 15 | 3/C #12 VFD CABLE | [16 empty] | 2 | G | 7 | 24 | 4 | 10
RM6-6MCC02 | 02L | RM6-MCC2-02L.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [20 empty] | 2 | L | 11 | 12 | 2 | 12
RM6-6MCC02 | 03A | RM6-BIN-101D.M1 | SURGE BIN 4 AGITATOR | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 3 | A | 1 | 36 | 6 | 6
RM6-6MCC02 | 03G | RM6-BIN-101C.M1 | SURGE BIN 3 AGITATOR | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 3 | G | 7 | 36 | 6 | 12
RM6-6MCC02 | 04A | RM6-BIN-101B.M1 | SURGE BIN 2 AGITATOR | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 4 | A | 1 | 36 | 6 | 6
RM6-6MCC02 | 04G | RM6-BIN-101A.M1 | SURGE BIN 1 AGITATOR | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 4 | G | 7 | 36 | 6 | 12
RM6-6MCC02 | 05A | RM6-PMP-103.M1 | DUAL AUGER CART 1 PUMP | VFD | 20 | 20 |  |  | 3 | 60 | 125 | 50 | 3/C #10 VFD CABLE | [16 empty] | 5 | A | 1 | 36 | 6 | 6
RM6-6MCC02 | 05G | RM6-PMP-104.M1 | DUAL AUGER CART 2 PUMP | VFD | 20 | 20 |  |  | 3 | 60 | 125 | 50 | 3/C #10 VFD CABLE | [16 empty] | 5 | G | 7 | 36 | 6 | 12
RM6-6MCC02 | 06A | RM6-SCR-201.M1 | VIBRATORY SCREENER | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 6 | A | 1 | 24 | 4 | 4
RM6-6MCC02 | 06E | RM6-MGR-101.M1 RM6-MGR-101.M2 | MIXER GRINDER 1 | VFD | 40 | 40 |  |  | 4 | 125 | 125 | 90 | 3/C #4 VFD CABLE | [16 empty] | 6 | E | 5 | 48 | 8 | 12
RM6-6MCC02 | 07A | RM6-CNV-201.M1 | INCLINE CONVEYOR | VFD | 3 | 5 |  |  | 2 | 15 | 125 | 15 | 3/C #12 VFD CABLE | [16 empty] | 7 | A | 1 | 24 | 4 | 4
RM6-6MCC02 | 07E | RM6-MGR-102.M1 RM6-MGR-102.M2 | MIXER GRINDER 2 | VFD | 40 | 40 |  |  | 4 | 125 | 125 | 90 | 3/C #4 VFD CABLE | [16 empty] | 7 | E | 5 | 48 | 8 | 12
RM6-6MCC02 | 08A | RM6-PMP-101.M1 | AUGER CART 1 PUMP | VFD | 25 | 25 |  |  | 3.5 | 60 | 125 | 60 | 3/C #8 VFD CABLE | [16 empty] | 8 | A | 1 | 42 | 7 | 7
RM6-6MCC02 | 08H | RM6-MTL-104.M1 | MIXER GRINDER 2 COLUMN DUMPER | FVR | 1.5 | 2 |  | 1 | 1.5 | 7 | 125 | N/A | 3/C #12 VFD CABLE | [16 empty] | 8 | H | 8 | 18 | 3 | 10
RM6-6MCC02 | 08L | RM6-MCC2-08L.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [20 empty] | 8 | L | 11 | 12 | 2 | 12
RM6-6MCC02 | 09A | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 9 | A | 1 | 12 | 2 | 2
RM6-6MCC02 | 09C | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 9 | C | 3 | 12 | 2 | 4
RM6-6MCC02 | 09E | RM6-MLT-102.M1 | COMBO TOTE DUMPER | FVNR | 7.5 | 10 |  | 1 | 1 | 30 | 125 | N/A | 3/C #12 VFD CABLE | [16 empty] | 9 | E | 5 | 12 | 2 | 6
RM6-6MCC02 | 09G | RM6-MGR-102.M3 | MIXER GRINDER 2 DISCHARGE SCREW | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 9 | G | 7 | 36 | 6 | 12
RM6-6MCC02 | 10A | RM6-GRR-101.M1 | FROZEN BLOCK BREAKER 1 | VFD | 60 | 60 |  |  | 6 | 200 | 250 | 125 | 3/C #2 VFD CABLE | [16 empty] | 10 | A | 1 | 72 | 12 | 12
RM6-6MCC02 | 11A | RM6-GRR-101.M2 | FROZEN BLOCK BREAKER 2 | VFD | 60 | 60 |  |  | 6 | 200 | 250 | 125 | 3/C #2 VFD CABLE | [16 empty] | 11 | A | 1 | 72 | 12 | 12
RM6-6MCC02 | 12A | RM6-SKD-101.M2 | VOTATOR PMP-202 COOKER 1 | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 12 | A | 1 | 24 | 4 | 4
RM6-6MCC02 | 12E | RM6-SKD-102.M2 | VOTATOR PMP-202 COOKER 2 | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 12 | E | 5 | 24 | 4 | 8
RM6-6MCC02 | 12J | RM6-CNV-105.M1 | SURGE BIN TAKEAWAY CONVEYOR | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 12 | J | 9 | 24 | 4 | 12
RM6-6MCC02 | 13A | SPARE | VFD - 1HP | VFD | 1 | 1 |  |  | 2 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [16 empty] | 13 | A | 1 | 24 | 4 | 4
RM6-6MCC02 | 13E | RM6-CNV-108.M1 | INCLINE CONVEYOR SCREW | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 13 | E | 5 | 36 | 6 | 10
RM6-6MCC02 | 13L | RM6-MCC2-13L.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [20 empty] | 13 | L | 11 | 12 | 2 | 12
RM6-6MCC02 | 14A | RM6-SKD-102.M1 | VOTATOR PMP-101 COOKER 1 | VFD | 3 | 5 |  |  | 2 | 15 | 125 | 15 | 3/C #12 VFD CABLE | [16 empty] | 14 | A | 1 | 24 | 4 | 4
RM6-6MCC02 | 14E | RM6-CNV-102.M1 | METAL DETECTOR BELT CONVEYOR | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 14 | E | 5 | 24 | 4 | 8
RM6-6MCC02 | 14J | RM6-SKD-103.M1 | VOTATOR PMP-201 COOKER 2 | VFD | 3 | 5 |  |  | 2 | 15 | 125 | 15 | 3/C #12 VFD CABLE | [16 empty] | 14 | J | 9 | 24 | 4 | 12
RM6-6MCC02 | 15A | RM6-SKD-103.M2 | VOTATOR PMP-202 COOKER 2 | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 10 | 3/C #12 VFD CABLE | [16 empty] | 15 | A | 1 | 24 | 4 | 4
RM6-6MCC02 | 15E | RM6-SKD-104.M1 | VOTATOR PMP-101 COOKER 2 | VFD | 3 | 5 |  |  | 2 | 15 | 125 | 15 | 3/C #12 VFD CABLE | [16 empty] | 15 | E | 5 | 24 | 4 | 8
RM6-6MCC02 | 15J | RM6-SKD-104.M2 | VOTATOR PMP-102 COOKER 2 | VFD | 2 | 2 |  |  | 2 | 15 | 125 | 15 | 3/C #12 VFD CABLE | [16 empty] | 15 | J | 9 | 24 | 4 | 12
RM6-6MCC02 | 16A | RM6-HTX-101.M1 | VOTATOR HX-101 COOKER 1 | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 16 | A | 1 | 36 | 6 | 6
RM6-6MCC02 | 16G | RM6-HTX-102.M1 | VOTATOR HX-102 COOKER 1 | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 16 | G | 7 | 36 | 6 | 12
RM6-6MCC02 | 17A | RM6-HTX-103.M1 | VOTATOR HX-103 COOKER 1 | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 17 | A | 1 | 36 | 6 | 6
RM6-6MCC02 | 17G | RM6-HTX-104.M1 | VOTATOR HX-104 COOKER 1 | VFD | 15 | 15 |  |  | 3 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 17 | G | 7 | 36 | 6 | 12
RM6-6MCC02 | 18A | SPACE | [6 empty] | 1 | [20 empty] | 18 | A | 1 | 12 | 2 | 2
RM6-6MCC02 | 18C | RM6-AGC-101.M1 | AUGER CART 1 AUGER 1 | VFD | 7.5 | 10 |  |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [16 empty] | 18 | C | 3 | 30 | 5 | 7
RM6-6MCC02 | 18H | RM6-AGC-101.M2 | AUGER CART 1 AUGER 2 | VFD | 7.5 | 10 |  |  | 2.5 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [16 empty] | 18 | H | 8 | 30 | 5 | 12
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
VTTRS-MCC1 | 01A | MAIN | INCOMING MCB | MAIN |  |  |  |  | 3.5 | 1200 | 1200 | N/A | [17 empty] | 1 | A | 1 | 42 | 7 | 7
VTTRS-MCC1 | 01H | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 1 | H | 8 | 6 | 1 | 8
VTTRS-MCC1 | 01J | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 1 | J | 9 | 12 | 2 | 10
VTTRS-MCC1 | 01L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 1 | L | 11 | 12 | 2 | 12
VTTRS-MCC1 | 02A | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 2 | A | 1 | 12 | 2 | 2
VTTRS-MCC1 | 02C | RL7-MCC1-PM | POWERMONITOR 5000 W/ ETHERNET | PM |  |  |  |  | 1.5 | N/A | N/A | 0.75 | [17 empty] | 2 | C | 3 | 18 | 3 | 5
VTTRS-MCC1 | 02F | HTX-101 | VOTATOR 1 | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | N/A | 3/C #6 VFD CABLE | [16 empty] | 2 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 03A | PMP-101 | B&F HOT WATER LOOP PUMP | VFD | 15 | 15 |  |  | 2.5 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 3 | A | 1 | 30 | 5 | 5
VTTRS-MCC1 | 03F | HTX-102 | VOTATOR 2 | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | N/A | 3/C #6 VFD CABLE | [16 empty] | 3 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 04A | PMP-102 | BOOSTER PUMP | VFD | 15 | 15 |  |  | 2.5 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 4 | A | 1 | 30 | 5 | 5
VTTRS-MCC1 | 04F | HTX-103 | VOTATOR 3 | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | N/A | 3/C #6 VFD CABLE | [16 empty] | 4 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 05A | RM5-MCC1-5A.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [20 empty] | 5 | A | 1 | 12 | 2 | 2
VTTRS-MCC1 | 05C | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 5 | C | 3 | 12 | 2 | 4
VTTRS-MCC1 | 05E | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 5 | E | 5 | 12 | 2 | 6
VTTRS-MCC1 | 05G | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 5 | G | 7 | 12 | 2 | 8
VTTRS-MCC1 | 05J | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 5 | J | 9 | 12 | 2 | 10
VTTRS-MCC1 | 05L | RM5-MCC1-5L.ENPS | ETHERNET SWITCH POWER SUPPLY | ENET_PS |  |  |  |  | 1 | [20 empty] | 5 | L | 11 | 12 | 2 | 12
VTTRS-MCC1 | 06A | PMP-106 | CHILLED WATER PUMP 2 | VFD | 15 | 15 |  |  | 2.5 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 6 | A | 1 | 30 | 5 | 5
VTTRS-MCC1 | 06F | HTX-105 | VOTATOR 5 | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | N/A | 3/C #6 VFD CABLE | [16 empty] | 6 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 07A | PMP-103 | CHILLED WATER PUMP 1 | VFD | 15 | 15 |  |  | 2.5 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 7 | A | 1 | 30 | 5 | 5
VTTRS-MCC1 | 07F | HTX-104 | VOTATOR 4 | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | N/A | 3/C #6 VFD CABLE | [16 empty] | 7 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 08A | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 8 | A | 1 | 6 | 1 | 1
VTTRS-MCC1 | 08B | SPARE | VFD - 10HP | VFD |  | 10 |  |  | 2 | 30 | 125 | 25 | [17 empty] | 8 | B | 2 | 24 | 4 | 5
VTTRS-MCC1 | 08F | HTX-106 | VOTATOR 6 | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | N/A | 3/C #6 VFD CABLE | [16 empty] | 8 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 09A | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 9 | A | 1 | 6 | 1 | 1
VTTRS-MCC1 | 09B | FHD-101 | FORMING HEAD | VFD | 7.5 | 7.5 |  |  | 2 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [16 empty] | 9 | B | 2 | 24 | 4 | 5
VTTRS-MCC1 | 09F | HTX-107 | VOTATOR 7 | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | N/A | 3/C #6 VFD CABLE | [16 empty] | 9 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 10A | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 10 | A | 1 | 6 | 1 | 1
VTTRS-MCC1 | 10B | PMP-10x | VOTATOR SKID HW CIRC PUMP | VFD |  |  |  |  | 2 | [20 empty] | 10 | B | 2 | 24 | 4 | 5
VTTRS-MCC1 | 10F | HTX-108 | VOTATOR 8 | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | N/A | 3/C #6 VFD CABLE | [16 empty] | 10 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 11A | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 11 | A | 1 | 12 | 2 | 2
VTTRS-MCC1 | 11C | PMP-104 | INJECTION PUMP 1 | VFD | 5 | 5 |  |  | 1.5 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 11 | C | 3 | 18 | 3 | 5
VTTRS-MCC1 | 11F | HTX-109 | VOTATOR 9 | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | N/A | 3/C #6 VFD CABLE | [16 empty] | 11 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 12A | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 12 | A | 1 | 12 | 2 | 2
VTTRS-MCC1 | 12C | SPARE | VFD - 5HP | VFD |  | 5 |  |  | 1.5 | 20 | 125 | 12 | [17 empty] | 12 | C | 3 | 18 | 3 | 5
VTTRS-MCC1 | 12F | HTX-110 | VOTATOR 10 | VFD | 30 | 30 |  |  | 3.5 | 100 | 125 | N/A | 3/C #6 VFD CABLE | [16 empty] | 12 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 13A | RM5-MCC1-13A.ENPS | ETHERNET SWITCH POWER SUPPLY | ENET_PS |  |  |  |  | 1 | [20 empty] | 13 | A | 1 | 12 | 2 | 2
VTTRS-MCC1 | 13C | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 13 | C | 3 | 12 | 2 | 4
VTTRS-MCC1 | 13E | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 13 | E | 5 | 6 | 1 | 5
VTTRS-MCC1 | 13F | CNV-101 | BATH CONVEYOR 1 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 13 | F | 6 | 24 | 4 | 9
VTTRS-MCC1 | 13K | PMP-106 | VOTATOR SKID MAKEUP WATER PUMP | VFD | 1 | 2 |  |  | 1.5 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [16 empty] | 13 | K | 10 | 18 | 3 | 12
VTTRS-MCC1 | 14A | SPARE | VFD - 2HP | VFD |  | 2 |  |  | 1.5 | 15 | 125 | 6 | [17 empty] | 14 | A | 1 | 18 | 3 | 3
VTTRS-MCC1 | 14D | SPARE | VFD - 2HP | VFD |  | 2 |  |  | 1.5 | 15 | 125 | 6 | [17 empty] | 14 | D | 4 | 18 | 3 | 6
VTTRS-MCC1 | 14G | SPARE | VFD - 5HP | VFD |  | 5 |  |  | 1.5 | 20 | 125 | 12 | [17 empty] | 14 | G | 7 | 18 | 3 | 9
VTTRS-MCC1 | 14K | SPARE | VFD - 5HP | VFD |  | 5 |  |  | 1.5 | 20 | 125 | 12 | [17 empty] | 14 | K | 10 | 18 | 3 | 12
VTTRS-MCC1 | 15A | SPARE | VFD - 2HP | VFD |  | 2 |  |  | 1.5 | 15 | 125 | 6 | [17 empty] | 15 | A | 1 | 18 | 3 | 3
VTTRS-MCC1 | 15D | SPARE | VFD - 2HP | VFD |  | 2 |  |  | 1.5 | 15 | 125 | 6 | [17 empty] | 15 | D | 4 | 18 | 3 | 6
VTTRS-MCC1 | 15G | PMP-109 | BATH 1 CIRCULATION PUMP | VFD | 1 | 2 |  |  | 1.5 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [16 empty] | 15 | G | 7 | 18 | 3 | 9
VTTRS-MCC1 | 15K | SPARE | VFD - 5HP | VFD |  | 5 |  |  | 1.5 | 20 | 125 | 12 | [17 empty] | 15 | K | 10 | 18 | 3 | 12
VTTRS-MCC1 | 16A | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 16 | A | 1 | 6 | 1 | 1
VTTRS-MCC1 | 16B | CNV-102 | BATH CONVEYOR 2 | VFD | 5 | 5 |  |  | 2 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 16 | B | 2 | 24 | 4 | 5
VTTRS-MCC1 | 16F | SPARE | VFD - 30HP | VFD |  | 30 |  |  | 3.5 | 100 | 125 | N/A | [17 empty] | 16 | F | 6 | 42 | 7 | 12
VTTRS-MCC1 | 17A | RM5-MCC1-5A.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [20 empty] | 17 | A | 1 | 12 | 2 | 2
VTTRS-MCC1 | 17C | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 17 | C | 3 | 6 | 1 | 3
VTTRS-MCC1 | 17D | SPARE | VFD - 5HP | VFD |  | 5 |  |  | 1.5 | 20 | 125 | 12 | [17 empty] | 17 | D | 4 | 18 | 3 | 6
VTTRS-MCC1 | 17G | SPARE | VFD - 5HP | VFD |  | 5 |  |  | 1.5 | 20 | 125 | 12 | [17 empty] | 17 | G | 7 | 18 | 3 | 9
VTTRS-MCC1 | 17K | SCR-101 | WASTE SEPARATOR DRUM | VFD | 5 | 5 |  |  | 1.5 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 17 | K | 10 | 18 | 3 | 12
VTTRS-MCC1 | 18A | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 18 | A | 1 | 12 | 2 | 2
VTTRS-MCC1 | 18C | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 18 | C | 3 | 12 | 2 | 4
VTTRS-MCC1 | 18E | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 18 | E | 5 | 12 | 2 | 6
VTTRS-MCC1 | 18G | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 18 | G | 7 | 12 | 2 | 8
VTTRS-MCC1 | 18J | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 18 | J | 9 | 12 | 2 | 10
VTTRS-MCC1 | 18L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 18 | L | 11 | 12 | 2 | 12
VTTRS-MCC2 | 01A | MAIN | INCOMING MCB | MAIN |  |  |  |  | 3.5 | 1200 | 1200 | N/A | [17 empty] | 1 | A | 1 | 42 | 7 | 7
VTTRS-MCC2 | 01H | RL7-MCC1-PM | POWERMONITOR 5000 W/ ETHERNET | PM |  |  |  |  | 1.5 | N/A | N/A | 0.75 | [17 empty] | 1 | H | 8 | 18 | 3 | 10
VTTRS-MCC2 | 01L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 1 | L | 11 | 12 | 2 | 12
VTTRS-MCC2 | 02A | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 2 | A | 1 | 12 | 2 | 2
VTTRS-MCC2 | 02C | MGR-001 | LEFT / RIGHT AUGER | VFD | (2) 20 | 50 |  |  | 5 | 125 | 125 | 100 | 3/C #10 VFD CABLE | [16 empty] | 2 | C | 3 | 60 | 10 | 12
VTTRS-MCC2 | 03A | SPARE | VFD - 15HP | VFD |  | 15 |  |  | 2.5 | 60 | 125 | 40 | [17 empty] | 3 | A | 1 | 30 | 5 | 5
VTTRS-MCC2 | 03F | SPARE | VFD - 30HP | VFD |  | 30 |  |  | 3.5 | 100 | 125 | N/A | [17 empty] | 3 | F | 6 | 42 | 7 | 12
VTTRS-MCC2 | 04A | GRR-001 | FROZEN GRINDER | VFD | 100 | 100 |  |  | 6 | 250 | 250 | 225 | 3/C #2/0 VFD CABLE | [16 empty] | 4 | A | 1 | 72 | 12 | 12
VTTRS-MCC2 | 05A | RM5-MCC2-5A.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [20 empty] | 5 | A | 1 | 12 | 2 | 2
VTTRS-MCC2 | 05C | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 5 | C | 3 | 12 | 2 | 4
VTTRS-MCC2 | 05E | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 5 | E | 5 | 12 | 2 | 6
VTTRS-MCC2 | 05G | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 5 | G | 7 | 12 | 2 | 8
VTTRS-MCC2 | 05J | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 5 | J | 9 | 12 | 2 | 10
VTTRS-MCC2 | 05L | RM5-MCC1-5L.ENPS | ETHERNET SWITCH POWER SUPPLY | ENET_PS |  |  |  |  | 1 | [20 empty] | 5 | L | 11 | 12 | 2 | 12
VTTRS-MCC2 | 06A | SPARE | VFD - 5HP | VFD |  | 5 |  |  | 1.5 | 20 | 125 | 12 | [17 empty] | 6 | A | 1 | 18 | 3 | 3
VTTRS-MCC2 | 06D | AGC-002.M1 | AUGER CART LEFT AUGER | VFD | 5 | 5 |  |  | 1.5 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 6 | D | 4 | 18 | 3 | 6
VTTRS-MCC2 | 06G | AGC-002.M2 | AUGER CART RIGHT AUGER | VFD | 5 | 5 |  |  | 1.5 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 6 | G | 7 | 18 | 3 | 9
VTTRS-MCC2 | 06K | CNV-001 | INCLINE BELT CONVEYOR | VFD | 5 | 5 |  |  | 1.5 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 6 | K | 10 | 18 | 3 | 12
VTTRS-MCC2 | 07A | CNV-002 | FB INCLINE / MD CONVEYOR | VFD | 10 | 10 |  |  | 2 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [16 empty] | 7 | A | 1 | 24 | 4 | 4
VTTRS-MCC2 | 07E | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | 30 | 125 | 25 | [17 empty] | 7 | E | 5 | 12 | 2 | 6
VTTRS-MCC2 | 07G | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 7 | G | 7 | 12 | 2 | 8
VTTRS-MCC2 | 07J | CNV-003 | INCLINE AUGER CONVEYOR | VFD | 10 | 10 |  |  | 2 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [16 empty] | 7 | J | 9 | 24 | 4 | 12
VTTRS-MCC2 | 08A | MGR-001 | DISCHARGE SCREW | VFD | 15 | 15 |  |  | 2.5 | 60 | 125 | 40 | 3/C #10 VFD CABLE | [16 empty] | 8 | A | 1 | 30 | 5 | 5
VTTRS-MCC2 | 08F | GRR-002 | FROZEN GRINDER SCREW | VFD | 40 | 40 |  |  | 3.5 | 125 | 125 | 100 | 3/C #4 VFD CABLE | [16 empty] | 8 | F | 6 | 42 | 7 | 12
VTTRS-MCC2 | 09A | MLT-004 | COLUMN DUMPER | FVR | 3 | 3 |  | 1 | 1.5 | 15 | 125 | N/A | 3/C #12 W/ GND | [16 empty] | 9 | A | 1 | 18 | 3 | 3
VTTRS-MCC2 | 09D | CNV-002 | INCLINE PIVOT AUGER | VFD | 2 | 2 |  |  | 1.5 | 15 | 125 | 6 | 3/C #12 VFD CABLE | [16 empty] | 9 | D | 4 | 18 | 3 | 6
VTTRS-MCC2 | 09G | TNK-001 | COOKING KETTLE MIXER | VFD | 5 | 5 |  |  | 1.5 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 9 | G | 7 | 18 | 3 | 9
VTTRS-MCC2 | 09K | AGR-001 | CHILLING KETTLE AGITATOR | VFD | 5 | 5 |  |  | 1.5 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 9 | K | 10 | 18 | 3 | 12
VTTRS-MCC2 | 10A | PMP-xxx | INCLINE AUGER HYDRAULIC PUMP | FVNR | 2 | 2 |  | 1 | 1 | 7 | 125 | N/A | 3/C #12 W/ GND | [16 empty] | 10 | A | 1 | 12 | 2 | 2
VTTRS-MCC2 | 10C | MLT-005 | COLUMN DUMPER | FVR | 3 | 3 |  | 1 | 1.5 | 15 | 125 | N/A | 3/C #12 W/ GND | [16 empty] | 10 | C | 3 | 18 | 3 | 5
VTTRS-MCC2 | 10F | SPACE | 6" SPACE | SPACE |  |  |  |  | 0.5 | [20 empty] | 10 | F | 6 | 6 | 1 | 6
VTTRS-MCC2 | 10G | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 10 | G | 7 | 12 | 2 | 8
VTTRS-MCC2 | 10J | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 10 | J | 9 | 12 | 2 | 10
VTTRS-MCC2 | 10L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 10 | L | 11 | 12 | 2 | 12
VTTRS-MCC2 | 11A | RM5-MCC2-11A.SW1 | ETHERNET SWITCH (20-PORT) | ENET_20 |  |  |  |  | 1 | [20 empty] | 11 | A | 1 | 12 | 2 | 2
VTTRS-MCC2 | 11C | AGC-001.M1 | AUGER CART 1 - LEFT AUGER | VFD | 5 | 5 |  |  | 1.5 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 11 | C | 3 | 18 | 3 | 5
VTTRS-MCC2 | 11F | AGC-001.M2 | AUGER CART 1 - RIGHT AUGER | VFD | 5 | 5 |  |  | 1.5 | 20 | 125 | 12 | 3/C #12 VFD CABLE | [16 empty] | 11 | F | 6 | 18 | 3 | 8
VTTRS-MCC2 | 11J | AGC-002.M3 | AUGER CART 2 - LEVELING RIBBON | VFD | 7.5 | 7.5 |  |  | 2 | 30 | 125 | 25 | 3/C #12 VFD CABLE | [16 empty] | 11 | J | 9 | 24 | 4 | 12
VTTRS-MCC2 | 12A | MLT-001 | TOTE DUMPER | FVNR | 10 | 10 |  | 1 | 1 | 30 | 125 | N/A | 3/C #12 W/ GND | [16 empty] | 12 | A | 1 | 12 | 2 | 2
VTTRS-MCC2 | 12C | ??? | TRACK | FVR | 1 | 1 |  |  | 1.5 | 3 | 125 | N/A | 3/C #12 W/ GND | [16 empty] | 12 | C | 3 | 18 | 3 | 5
VTTRS-MCC2 | 12F | AGC-001.M3 | AUGER CART 1 - PUMP | VFD | 40 | 40 |  |  | 3.5 | 125 | 125 | 100 | 3/C #4 VFD CABLE | [16 empty] | 12 | F | 6 | 42 | 7 | 12
VTTRS-MCC2 | 13A | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 13 | A | 1 | 12 | 2 | 2
VTTRS-MCC2 | 13C | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 13 | C | 3 | 12 | 2 | 4
VTTRS-MCC2 | 13E | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 13 | E | 5 | 12 | 2 | 6
VTTRS-MCC2 | 13G | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 13 | G | 7 | 12 | 2 | 8
VTTRS-MCC2 | 13J | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 13 | J | 9 | 12 | 2 | 10
VTTRS-MCC2 | 13L | SPACE | 12" SPACE | SPACE |  |  |  |  | 1 | [20 empty] | 13 | L | 11 | 12 | 2 | 12
VTTRS-MCC2 | 14A | GRR-001 | FROZEN GRINDER | VFD | 215 | 250 |  |  | 6 | 400 | 400 | 400 | 3/C 400 MCM VFD CABLE | [16 empty] | 14 | A | 1 | 72 | 12 | 12
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
UNUSED | 01A | SPARE | VFD - 75HP | VFD |  | 75 |  |  | 6 | 250 | 250 | 175 | [17 empty] | 1 | A | 1 | 72 | 12 | 12
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A
[9 empty] | 0 | [20 empty] | #VALUE! |  | #N/A | #VALUE! | 0 | #N/A

## NP Needed
RL7-6MCC01 | MASTER NP | RL7-6MCC1 | ROLL LINE 7
RL7-6MCC02 | 02C | RL7-MCC2-2C.PS1 | ETHERNET SWITCH POWER SUPPLY
RL7-6MCC02 | 16A | RL7-MCC2-16A.SW1 RL7-MCC2-16A.SW2 | ETHERNET SWITCHES
RL7-6MCC02 | 19A | RL7-MCC2-19A.PS1 | ETHERNET SWITCH POWER SUPPLY

## PNL-DVC
EQUIPMENT ID | TYPE | EQUIPMENT DESCRIPTION | LOCATION | MOUNTING | LINE | UPS PANEL_CKT | NOTES | RACEWAYS COMPLETE | CKT PULLED | CKT TERMED | PANEL / DEVICE ENERGIZED | COMMS PULLED | COMMS TERMED | COMMS TESTED | COMMS CONFIG | COMMS GOOD
RL-HWS4-CP1 | CP | HAND WEIGH STATION 4 CONTROL PANEL | DRY BATCH | WALL
RL-HWS4-HMI1 | HMI | HAND WEIGH STATION 4 HMI | DRY BATCH | POST |  |  | POST INCLUDED W/ 4XXTREME ENCLOSURE
RL-HWS4-QR1 | QR | HAND WEIGH STATION 4 QR SCANNER | DRY BATCH
RL-HWS4-SCN1 | SCN | HAND WEIGH STATION 4 BARCODE SCANNER | DRY BATCH
RL-HWS4-ZEB1 | ZEB | HAND WEIGH STATION 4 ZEBRA PRINTER | DRY BATCH
RL-HWS4-FSCL1 | FSCL | HAND WEIGH STATION 4 FLOOR SCALE | DRY BATCH
RL-HWS4-TSCL1 | TSCL | HAND WEIGH STATION 4 TABLE SCALE 1 | DRY BATCH
RL-HWS4-TSCL2 | TSCL | HAND WEIGH STATION 4 TABLE SCALE 2 | DRY BATCH
RL-HWS5-CP1 | CP | HAND WEIGH STATION 5 CONTROL PANEL | DRY BATCH | WALL
RL-HWS5-HMI1 | HMI | HAND WEIGH STATION 5 HMI | DRY BATCH | POST |  |  | POST INCLUDED W/ 4XXTREME ENCLOSURE
RL-HWS5-QR1 | QR | HAND WEIGH STATION 5 QR SCANNER | DRY BATCH
RL-HWS5-SCN1 | SCN | HAND WEIGH STATION 5 BARCODE SCANNER | DRY BATCH
RL-HWS5-ZEB1 | ZEB | HAND WEIGH STATION 5 ZEBRA PRINTER | DRY BATCH
RL-HWS5-FSCL1 | FSCL | HAND WEIGH STATION 5 FLOOR SCALE | DRY BATCH
RL-HWS5-TSCL1 | TSCL | HAND WEIGH STATION 5 TABLE SCALE 1 | DRY BATCH
RL-HWS5-TSCL2 | TSCL | HAND WEIGH STATION 5 TABLE SCALE 2 | DRY BATCH
RL-HWS6-CP1 | CP | HAND WEIGH STATION 6 CONTROL PANEL | DRY BATCH | WALL
RL-HWS6-HMI1 | HMI | HAND WEIGH STATION 6 HMI | DRY BATCH | POST |  |  | POST INCLUDED W/ 4XXTREME ENCLOSURE
RL-HWS6-QR1 | QR | HAND WEIGH STATION 6 QR SCANNER | DRY BATCH
RL-HWS6-SCN1 | SCN | HAND WEIGH STATION 6 BARCODE SCANNER | DRY BATCH
RL-HWS6-ZEB1 | ZEB | HAND WEIGH STATION 6 ZEBRA PRINTER | DRY BATCH
RL-HWS6-FSCL1 | FSCL | HAND WEIGH STATION 6 FLOOR SCALE | DRY BATCH
RL-HWS6-TSCL1 | TSCL | HAND WEIGH STATION 6 TABLE SCALE 1 | DRY BATCH
RL-HWS6-TSCL2 | TSCL | HAND WEIGH STATION 6 TABLE SCALE 2 | DRY BATCH
RL-LWS-HMI2 | HMI | LIQUID WEIGH STATION HMI 2 | DRY BATCH
RL7-BINA-RIO1 | RIO | SURGE BINS 1 & 2 RIO | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-BINB-RIO1 | RIO | SURGE BINS 3 & 4 RIO | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-BINS-HMI1 | HMI | SURGE BINS PLATFORM HMI | GRINDING AND COOKING | PLATFORM | LINE 7 |  | UPDATED TAG - PBK-HMI2 -> BINS-HMI1
RL7-BINS-RIO1 | RIO | SURGE BIN SUPPLY CONVEYOR RIO | GRINDING AND COOKING | EQUIPMENT | LINE 7 |  | NEW
RL7-BRED-RIO1 | RIO | BREDDO MIXER RIO | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-BRED-HMI1 | HMI | BREDDO MIXER HMI | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-BRED-QR1 | QR | BREDDO MIXER PLATFORM QR SCANNER | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-BRED-QR2 | QR | BREDDO DUMPER QR SCANNER | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-CIP-HMI1 | HMI | CIP SKID HMI | CIP | WALL | LINE 7
RL7-CKR1-RIO1 | RIO | COOKER 1 RIO | GRINDING AND COOKING | EQUIPMENT | LINE 7
RL7-CKR1-HMI1 | HMI | COOKER 1 HMI | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-CKR1-QR1 | QR | COOKER 1 QR SCANNER | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-CKR2-RIO1 | RIO | COOKER 2 RIO | GRINDING AND COOKING | EQUIPMENT | LINE 7
RL7-CKR2-HMI1 | HMI | COOKER 2 HMI | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-CKR2-QR1 | QR | COOKER 2 QR SCANNER | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-DAGC1-RIO1 | RIO | DISCHARGE AUGER CART | FILLING AND CHILLING | EQUIPMENT | LINE 7
RL7-FAGC1-RIO1 | RIO | FRESH AUGER CART 1 RIO | GRINDING AND COOKING | EQUIPMENT | LINE 7
RL7-FAGC2-RIO1 | RIO | FRESH AUGER CART 2 RIO | GRINDING AND COOKING | EQUIPMENT | LINE 7
RL7-FAGC-HMI1 | HMI | FRESH AUGER CARTS HMI | GRINDING AND COOKING | STAND | LINE 7
RL7-FAGC-SCN1 | SCN | FRESH AUGER CARTS BARCODE SCANNER | GRINDING AND COOKING |  | LINE 7
RL7-INSTL-RIO1 | RIO | INTERSTITIAL RIO - GRINDING & COOKING | RL7 PROCESS CORRIDOR | WALL | LINE 7
RL7-INSTL-RIO2 | RIO | INTERSTITIAL RIO - CHILLING & PACKAGING | RL7 PROCESS CORRIDOR | WALL | LINE 7
RL7-IPA1-RIO1 | RIO | INCLINE PIVOT AUGER 1 RIO | GRINDING AND COOKING | EQUIPMENT |  |  | NEW
RL7-IPA2-RIO1 | RIO | INCLINE PIVOT AUGER 2 RIO | GRINDING AND COOKING | EQUIPMENT |  |  | NEW
RL7-LAS-HMI1 | HMI | LACTIC ACID SKID HMI | HEAT EXCHANGE / LACTIC ACID | WALL | LINE 7
RL7-LAS-SCN1 | SCN | LACTIC ACID SKID BARCODE SCANNER | HEAT EXCHANGE / LACTIC ACID |  | LINE 7 | RL7-LAS-HMI1_CB10051
RL7-LAS-TSCL1 | TSCL | LACTIC ACID SKID TABLE SCALE | HEAT EXCHANGE / LACTIC ACID |  | LINE 7
RL7-LINE-HMI1 | HMI | GRINDING AND COOKING AREA HMI'S | GRINDING AND COOKING | FLOOR MOUNTED | LINE 7
RL7-LINE-PLC | PLC | MAIN PLC CABINET | MDF ROOM | RACK | LINE 7
RL7-PRM-RIO1 | RIO | PRE-MIXER RIO | GRINDING AND COOKING | EQUIPMENT | LINE 7 |  | UPDATED TAG - MISC -> PRM
RL7-PRM-HMI1 | HMI | PRE-MIXER HMI | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-PRM-QR1 | QR | PRE-MIXER QR SCANNER | GRINDING AND COOKING | PLATFORM | LINE 7 | RL7-PRM-HMI1_CB10051
RL7-PBK-RIO1 | RIO | FROZEN GRINDER RIO | GRINDING AND COOKING | PLATFORM | LINE 7
RL7-PBK-HMI1 | HMI | FROZEN GRINDER HMI | GRINDING AND COOKING | STAND | LINE 7
RL7-PBK-SCN1 | SCN | FROZEN GRINDER BARCODE SCANNER | GRINDING AND COOKING |  | LINE 7 | RL7-PBK-HMI1_CB10049
RL7-PKOUT-HMI1 | HMI | PACKAGING HMI | PACKAGING | POST | LINE 7 |  | POST INCLUDED W/ 4XXTREME ENCLOSURE
RL7-PKOUT-RIO1 | RIO | PACKAGING RIO | PACKAGING | STAND | LINE 7 |  | NEW
RL7-RWK-HMI1 | HMI | HOT REWORK HMI | FILLING AND CHILLING | STAND | LINE 7
RL7-RWK-QR1 | QR | HOT REWORK QR SCANNER | FILLING AND CHILLING |  | LINE 7 | RL7-RWK-HMI1_CB10060
RL7-RWK-SCN1 | SCN | HOT REWORK BARCODE SCANNER | FILLING AND CHILLING |  | LINE 7 | RL7-RWK-HMI1_CB10064
RL7-RWK-ZEB1 | ZEB | HOT REWORK ZEBRA PRINTER | FILLING AND CHILLING |  | LINE 7 | RL7-RWK-HMI1_CB10058
RL7-RWK-FSCL1 | FSCL | HOT REWORK FLOOR SCALE | FILLING AND CHILLING |  | LINE 7 | RL7-RWK-HMI1_CB10014
RL7-SERP-RIO1 | RIO | SERPENTINE RIO 1 | FILLING AND CHILLING | STAND | LINE 7
RL7-SERP-RIO2 | RIO | SERPENTINE RIO 2 | FILLING AND CHILLING | STAND | LINE 7
RL7-SERP-HMI1 | HMI | SERPENTINE HMI | FILLING AND CHILLING | WALL | LINE 7
RL7-VEG-HMI1 | HMI | VEGGIE STATION HMI | GRINDING AND COOKING | WALL | LINE 7 |  | UPDATED TAG - INC -> VEG
RL7-VEG-QR1 | QR | VEGGIE STATION QR SCANNER | GRINDING AND COOKING |  | LINE 7 |  | UPDATED TAG - INC -> VEG
RL7-VEG-SCN1 | SCN | VEGGIE STATION BARCODE SCANNER | GRINDING AND COOKING |  | LINE 7 |  | UPDATED TAG - INC -> VEG
RL7-VEG-ZEB1 | ZEB | VEGGIE STATION ZEBRA PRINTER | GRINDING AND COOKING |  | LINE 7 |  | UPDATED TAG - INC -> VEG
RL7-VEG-FSCL1 | FSCL | VEGGIE STATION FLOOR SCALE | GRINDING AND COOKING |  | LINE 7 |  | UPDATED TAG - INC -> VEG
RL7-MCC1-2A.SW1 | SWITCH | 7MCC01 BUCKET 2A, NETWORK SWITCH #1 | UPPER LEVEL EAST-WEST CORRIDOR | INSIDE MCC | LINE 7 | 6UL1A_2 & 6UL1A_5
RL7-MCC1-2A.SW2 | SWITCH | 7MCC01 BUCKET 2A, NETWORK SWITCH #2 | UPPER LEVEL EAST-WEST CORRIDOR | INSIDE MCC | LINE 7 | 6UL1A_2 & 6UL1A_5
RL7-MCC1-14A.SW1 | SWITCH | 7MCC01 BUCKET 14A, NETWORK SWITCH #1 | UPPER LEVEL EAST-WEST CORRIDOR | INSIDE MCC | LINE 7 | 6UL1A_2 & 6UL1A_5
RL7-MCC1-14A.SW2 | SWITCH | 7MCC01 BUCKET 14A, NETWORK SWITCH #2 | UPPER LEVEL EAST-WEST CORRIDOR | INSIDE MCC | LINE 7 | 6UL1A_2 & 6UL1A_5
RL7-MCC2-2A.SW1 | SWITCH | 7MCC02 BUCKET 2A, NETWORK SWITCH #1 | UPPER LEVEL EAST-WEST CORRIDOR | INSIDE MCC | LINE 7 | 6UL1A_1 & 6UL1A_3
RL7-MCC2-12A.SW1 | SWITCH | 7MCC02 BUCKET 12A, NETWORK SWITCH #1 | UPPER LEVEL EAST-WEST CORRIDOR | INSIDE MCC | LINE 7 | 6UL1A_1 & 6UL1A_3
RL7-MCC2-16A.SW1 | SWITCH | 7MCC02 BUCKET 16A, NETWORK SWITCH #1 | UPPER LEVEL EAST-WEST CORRIDOR | INSIDE MCC | LINE 7 | 6UL1A_7 & 6UL1A_8
RL7-MCC2-16A.SW2 | SWITCH | 7MCC02 BUCKET 16A, NETWORK SWITCH #2 | UPPER LEVEL EAST-WEST CORRIDOR | INSIDE MCC | LINE 7 | 6UL1A_7 & 6UL1A_8
RL7-MCC3-2A.SW1 | SWITCH | 7MCC03 BUCKET 2A, NETWORK SWITCH #1 | UPPER LEVEL EAST-WEST CORRIDOR | INSIDE MCC | LINE 7 | 6UL1A_4 & 6UL1A_6
RL7-MCC3-16A.SW1 | SWITCH | 7MCC03 BUCKET 16A, NETWORK SWITCH #1 | UPPER LEVEL EAST-WEST CORRIDOR | INSIDE MCC | LINE 7 | 6UL1A_4 & 6UL1A_6

## Prog Over Time
WEEK | DATE | DEVICE INSTALLED | DEVICE TAGGED | CA INSTALLED | RACEWAYS COMPLETE | WIRE PULLED | WIRE TERMED | WIRE TAGGED | POINT TO POINT | IO CHECK | IO GOOD
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16

## PROGRESS
--

## Helper
UnitLetter | UnitIndex | RevitFamily | FamilyType | FamilyGraphics
A | 1 | Oneline_Ensw | PS_1Ckt-CPT | Motor
B | 2 | Oneline_Ensw_Power_Supply | PS_1Ckt-External-Power | Motor w/ Disc
C | 3 | Oneline_Feeder_Panel | PS_2Ckt-External-Power | Heater
D | 4 | Oneline_Feeder_Sub-Panel | Feeder_Panel | Power-Meter
E | 5 | Oneline_Feeder_Sub-Xfmr | Feeder_Panel-w-Disc
F | 6 | Oneline_MCC | Feeder_Space
G | 7 | Oneline_Motor | Feeder_Spare
H | 8 |  | Feeder_XFMR
J | 9 |  | Graphics_Power-Meter
K | 10 |  | MCC_MB-Bus1
L | 11 |  | MCC_MB-Bus2
M | 12 |  | MCC_MB-Bus3
MCC_MB-Bus4
MCC_MLO-Bus1
MCC_MLO-Bus2
MCC_MLO-Bus3
MCC_MLO-Bus4
Motor_FVNR
Motor_FVR
Motor_Soft-Start
Motor_VFD
Motor_VFD-w-Fuse
Motor_VFD-w-Fuse-Line-Filt
Motor_VFD-w-Fuse-Line-Load-Filt
Motor_VFD-w-Fuse-Load-Filt
Motor_VFD-w-Fuse-Load-Filter-2OL
Switch_10-Port
Switch_20-Port
Switch_30-Port

## MCC Elevs
RL7-6MCC01 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
| A | 01A MAIN INCOMING MCB | 2A RL7-MCC1-2A.SW1 RL7-MCC1-2A.SW2 ETHERNET SWITCH (10-PORT) ETHERNET SWITCH (20-PORT) | 03A SPARE VFD - 60HP | 04A RL7-GRR-101.M1 FINISH GRINDER | 05A SPARE VFD - 10HP | 06A RL7-CNV-112.M1 SURGE BIN TAKE AWAY CONVEYOR | 07A RL7-CNV-113.M1 INCLINE BELT CONVEYOR 1 | 08A RL7-BIN-101.M1 SURGE BIN 1 UPPER AGITATOR | 09A RL7-BIN-102.M1 SURGE BIN 2 UPPER AGITATOR | 10A RL7-BIN-103.M1 SURGE BIN 3 UPPER AGITATOR | 11A RL7-BIN-104.M1 SURGE BIN 4 UPPER AGITATOR | 12A RL7-CNV-110.M1 METAL DETECTOR CONVEYOR | 13A RL7-CNV-114.M2 INCLINE PIVOT AUGER 1 HYDRAULIC PUMP | 14A RL7-MCC1-14A.SW1 RL7-MCC1-14A.SW2 ETHERNET SWITCH (10-PORT) ETHERNET SWITCH (20-PORT) | 15A RL7-PMP-101.M1 FRESH AUGER CART 1 - PUMP | 16A RL7-MLT-104.M1 FRESH AUGER CART 1 - COMBO DUMPER | 17A RL7-GRR-103.M1 FROZEN BLOCK CRUSHER | 18A RL7-GRR-103.M2 FROZEN BLOCK CRUSHER
B
| C | 2: 02C RL7-MCC1-2C.PS1 ETHERNET SWITCH POWER SUPPLY; 13: 13C RL7-CNV-114.M1 INCLINE PIVOT AUGER 1; 14: 14C 12" SPACE; 16: 16C RL7-MLT-105.M1 FRESH AUGER CART 2 - COMBO DUMPER
D
| E | 2: 02E 6" SPACE; 6: 06E RL7-CNV-115.M1 INCLINE BELT CONVEYOR 2; 7: 07E SPARE VFD - 2HP; 12: 12E 6" SPACE; 14: 14E RL7-AGC-101.M1 FRESH AUGER CART 1 - AUGER 1; 16: 16E RL7-AGC-102.M1 FRESH AUGER CART 2 - AUGER 1
| F | 2: 02F SPARE SZ1 FVNR - 7.5HP; 5: 05F SPARE VFD - 25HP; 8: 08F 12" SPACE; 9: 09F 12" SPACE; 10: 10F 12" SPACE; 11: 11F 12" SPACE; 12: 12F RL7-CNV-109.M1 INCLINE AUGER CONVEYOR
| G | 15: 15G RL7-PMP-102.M1 FRESH AUGER CART 2 - PUMP
| H | 1: 01H RL7-MCC1-PM POWERMONITOR 5000 W/ ETHERNET; 2: 02H SPARE VFD - 10HP; 8: 08H RL7-BIN-101.M2 SURGE BIN 1 AUGER; 9: 09H RL7-BIN-102.M2 SURGE BIN 2 AUGER; 10: 10H RL7-BIN-103.M2 SURGE BIN 3 AUGER; 11: 11H RL7-BIN-104.M2 SURGE BIN 4 AUGER; 13: 13H 6" SPACE
| J | 6: 06J RL7-CNV-116.M1 ROTOCLAW BELT CONVEYOR; 7: 07J RL7-CNV-111.M1 SURGE BIN SUPPLY CONVEYOR; 13: 13J RL7-CNV-114.M3 INCLINE PIVOT AUGER 1 SLIDE TRACK; 14: 14J RL7-AGC-101.M2 FRESH AUGER CART 1 - AUGER 2; 16: 16J RL7-AGC-102.M2 FRESH AUGER CART 2 - AUGER 2
K
| L | 1: 01L SPARE SZ1 FVNR - 1.5HP
M
RL7-6MCC02 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
| A | 01A MAIN INCOMING MCB | 02A RL7-MCC2-2A.SW1 ETHERNET SWITCH (20-PORT) | 03A RL7-CKR-101.M1 COOKER 1 - AGITATOR 1 (LEFT) | 04A RL7-CKR-101.M2 COOKER 1 - AGITATOR 2 (RIGHT) | 05A RL7-CKR-102.M1 COOKER 2 - AGITATOR 1 (LEFT) | 06A RL7-SKD-101.M1 BREDDO MIXER | 07A RL7-CKR-102.M2 COOKER 2 - AGITATOR 2 (RIGHT) | 08A RL7-SKD-101.M2 BREDDO MIXER AGITATOR | 09A RL7-FAN-103.M1 COOKER 1 HOOD EXHAUST FAN | 10A RL7-FAN-104.M1 COOKER 2 HOOD EXHAUST FAN | 11A 18" SPACE | 12A RL7-MCC2-12A.SW1 ETHERNET SWITCH (20-PORT) | 13A RL7-PRM-101.M2 RL7-PRM-101.M3 PRE-MIXER AGITATORS | 14A RL7-PMP-106.M1 PRE-MIXER PUMP | 15A 6" SPACE | 16A RL7-MCC2-16A.SW1 RL7-MCC2-16A.SW2 ETHERNET SWITCHES (10P & 20P) | 17A SPARE SZ1 FVNR - 1.5HP | 18A RL7-CNV-106.M2 INCLINE PIVOT AUGER 2 HYDRAULIC PUMP | 19A RL7-MCC2-19A.PS1 ETHERNET SWITCH POWER SUPPLY
B
| C | 2: 02C RL7-MCC2-2C.PS1 ETHERNET SWITCH POWER SUPPLY; 12: 12C SPARE SZ1 FVNR - 5HP; 15: 15C RL7-MLT-107.M1 COOKER 1 - COLUMN DUMPER; 16: 16C SPARE VFD - 5HP; 17: 17C SPARE VFD - 2HP; 18: 18C RL7-CNV-106.M3 INCLINE PIVOT AUGER 2 SLIDE TRACK; 19: 19C SPARE VFD - 10HP
| D | 11: 11D RL7-SKD-102.M1 LACTIC ACID SKID PUMP
| E | 2: 02E 6" SPACE; 8: 08E 12" SPACE; 9: 09E 12" SPACE; 10: 10E RL7-PMP-103.M1 BREDDO MIXER PUMP; 12: 12E RL7-FAN-101.M1 COOKER 1 - EXHAUST FAN
| F | 2: 02F SPARE VFD - 25HP; 15: 15F RL7-MLT-108.M1 COOKER 2 - COLUMN DUMPER
| G | 8: 08G RL7-PMP-104.M1 COOKER 1 - PUMP; 9: 09G RL7-PMP-105.M1 COOKER 2 - PUMP; 16: 16G RL7-MLT-106.M1 PRE-MIXER COLUMN DUMPER; 17: 17G SPARE VFD - 10HP; 18: 18G RL7-CNV-106.M1 INCLINE PIVOT AUGER 2
| H | 1: 01H RL7-MCC2-PM POWERMONITOR 5000 W/ ETHERNET; 3: 03H SPARE VFD - 2HP; 4: 04H SPARE VFD - 2HP; 5: 05H SPARE VFD - 2HP; 7: 07H RL7-PRM-101.M1 PRE-MIXER DISCHARGE SCREW; 11: 11H RL7-PMP-108.M1 HOT WATER JACKET PUMP; 19: 19H SPARE VFD - 10HP
| J | 12: 12J RL7-FAN-102.M1 COOKER 2 - EXHAUST FAN; 15: 15J 12" SPACE
| K | 16: 16K 18" SPACE
| L | 1: 01L RL7-DRM-101.M1 BREDDO DUMPER; 10: 10L 12" SPACE; 15: 15L 12" SPACE
| M | 3: 03M 6" SPACE; 4: 04M 6" SPACE; 5: 05M 6" SPACE; 17: 17M 6" SPACE; 18: 18M 6" SPACE
RL7-6MCC03 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
| A | 01A MAIN INCOMING MCB | 02A RL7-MCC3-2A.SW1 ETHERNET SWITCH (20-PORT) | 03A RL7-CNV-201.M1 ROLL FILLER DISCHARGE CONVEYOR | 04A RL7-AGC-201.M1 DISCHARGE AUGER CART - LEVELING RIBBON | 05A 12" SPACE | 06A RL7-CNV-205.M1 SERPENTINE DISCHARGE CONVEYOR 1 | 07A RL7-CHR-201.M1 SERPENTINE MAIN DRIVE | 08A RL7-PMP-203.M1 SERPENTINE HEX 1 PUMP | 09A RL7-PMP-204.M1 SERPENTINE RECIRC 1 PUMP | 10A RL7-PMP-205.M1 SERPENTINE HEX 2 PUMP | 11A RL7-PMP-206.M1 SERPENTINE RECIRC 2 PUMP | 12A RL7-PMP-207.M1 SERPENTINE HEX 3 PUMP | 13A 12" SPACE | 14A SPARE VFD - 1HP | 15A RL7-CNV-402.M1 METERING CONVEYOR 1 | 16A RL7-MCC3-16A.SW1 ETHERNET SWITCH (20-PORT)
B
| C | 2: 02C RL7-MCC3-2C.PS1 ETHERNET SWITCH POWER SUPPLY; 05M 6" SPACE 5: 05C RL7-PMP-201.M1 DISCHARGE AUGER CART PUMP; 05M 6" SPACE 13: 13C 12" SPACE; 05M 6" SPACE 16: 16C RL7-CNV-404.M1 CASE PACKER INFEED CONVEYOR
D
| E | 2: 02E SPARE VFD - 1HP; 03M 6" SPACE 3: 03E RL7-CNV-203.M1 SERPENTINE INFEED CONVEYOR 2; 04M 6" SPACE 4: 04E 6" SPACE; 05M 6" SPACE 6: 06E RL7-CNV-202.M1 SERPENTINE INFEED CONVEYOR 1; 05M 6" SPACE 13: 13E RL7-FTR-205.M1 SERPENTINE ZONE 2A FILTER; 05M 6" SPACE 14: 14E SPARE VFD - 1HP; 05M 6" SPACE 15: 15E RL7-CNV-401.M1 INSPECTION CONVEYOR
| F | 04M 6" SPACE 4: 04F RL7-SKD-201.M1 CLEAN ASSIST FOAM PUMP; 05M 6" SPACE 7: 07F 6" SPACE
| G | 05M 6" SPACE 7: 07G SPARE VFD - 20HP; 05M 6" SPACE 16: 16G RL7-FAN-201.M1 AIR KNIFE BLOWER
| H | 1: 01H RL7-MCC3-PM POWERMONITOR 5000 W/ ETHERNET; 05M 6" SPACE 5: 05H RL7-AGC-201.M2 DISCHARGE AUGER CART AUGER
| J | 2: 02J SPARE VFD - 5HP; 03M 6" SPACE 3: 03J RL7-CNV-204.M1 SERPENTINE INFEED CONVEYOR 3; 05M 6" SPACE 6: 06J RL7-CNV-403.M1 METERING CONVEYOR 2; 05M 6" SPACE 13: 13J RL7-FTR-207.M1 SERPENTINE ZONE 2B FILTER; 05M 6" SPACE 14: 14J SPARE VFD - 1HP; 05M 6" SPACE 15: 15J RL7-CNV-206.M1 SERPENTINE DISCHARGE CONVEYOR 2
K
| L | 1: 01L 12" SPACE; 04M 6" SPACE 4: 04L 12" SPACE
M
RM6-6MCC01 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
| A | 01A MAIN INCOMING MCB | 02A RM6-CNV-101.M1 INCLINE AUGER CONVEYOR | 03A RM6-GRR-105.M1 STEAM COOKER 1 DE-CLUMPER | 04A RM6-CKR-101.M1 STEAM COOKER 1 STEAM BELT 1 | 05A RM6-FAN-101.M1 STEAM COOKER 1 EXHAUST FAN 1 | 06A RM6-BIN-101B.M2 SURGE BIN 2 AUGER | 07A RM6-GRR-106.M1 STEAM COOKER 2 DE-CLUMPER | 08A RM6-AGC-103.M2 DUAL AUGER CART 1 AUGER 1 | 09A RM6-CKR-102.M2 STEAM COOKER 2 STEAM BELT 2 | 10A RM6-AGC.103.M4 DUAL AUGER CART 1 SLIDING TRACK | 11A RM6-GRR-102.M1 GRINDER | 12A RM6-SLT-201.M2 SLITTER | 13A RM6-CRT-201.M1 VINEGAR SUPPLE CART | 14A RM6-BIN-101D.M2 SURGE BIN 4 AUGER | 15A RM6-BIN-101A.M2 SURGE BIN 1 AUGER | 16A SPARE VFD - 2HP | 17A RM6-FAN-104.M1 STEAM COOKER 2 EXHAUST FAN 1 | 18A RM6-AGC-104.M3 DUAL AUGER CART 2 AUGER 2 | 19A SPARE VFD - 5HP
B
| C | 6: 06C RM6-CNV-112.M1 STEAM COOKER 1 DISCHARGE CONVEYOR
D
| E |  |  | 03E RM6-BIN-101C.M2 SURGE BIN 3 AUGER | 04E RM6-WWL-101.M1 RM6-SHR-101.M1 STEAM COOKER 1 WATERWHEEL/SPREADER MOTOR 1 | 05E RM6-FAN-102.M1 STEAM COOKER 1 EXHAUST FAN 2 |  | 07E RM6-CKR-102.M1 STEAM COOKER 2 STEAM BELT 1 | 08E RM6-AGC-103.M3 DUAL AUGER CART 1 AUGER 2 | 09E RM6-CNV-115.M1 STEAM COOKER 2 DISCHARGE CONVEYOR | 10E RM6-AGC-104.M4 DUAL AUGER CART 2 SLIDING TRACK |  | 12E 6" SPACE | 13E 6" SPACE |  |  | 16E RM6-CNV-104.M1 SURGE BIN SUPPLY CONVEYOR | 17E RM6-FAN-105.M1 STEAM COOKER 2 EXHAUST FAN 2 | 18E RM6-MLT-103.M1 MIXER GRINDER 1 COLUMN DUMPER | 19E RM6_82 CIP TANK STARTER
| F | 12: 12F RM6-MGR-101.M4 MIXER GRINDER 1 GRINDER; 13: 13F RM6-MGR-102.M4 MIXER GRINDER 2 GRINDER
| G | 14: 14G SPARE VFD - 2HP; 15: 15G 6" SPACE
| H | 1: 01H RM6-MCC1-PM POWERMONITOR 5000 W/ ETHERNET; 2: 02H RM6-MCC1-02H.PS1 ETHERNET SWITCH POWER SUPPLY; 15: 15H RM6-AGC-103.M1 DUAL AUGER CART 1 LEVELING RIBON; 18: 18H RM6-AGC-104.M1 DUAL AUGER CART 2 LEVELING RIBON; 19: 19H 6" SPACE
| J | 4: 04J RM6-CKR-101.M2 STEAM COOKER 1 STEAM BELT 2; 5: 05J RM6-FAN-103.M1 STEAM COOKER 1 EXHAUST FAN 3; 7: 07J RM6-WWL-102.M1 RM6-SHR-102.M1 STEAM COOKER 2 WATERWHEEL/SPREADER MOTOR 1; 8: 08J RM6-AGC-104.M2 DUAL AUGER CART 2 AUGER 1; 9: 09J RM6-CNV-107.M1 INCLINED BELT CONVEYOR; 10: 10J RM6-CNV-108.M3 INCLINE CONVEYOR SLIDE TRACK; 16: 16J RM6-CNV-108.M2 INCLINE CONVEYOR HYDRAULICS; 17: 17J RM6-FAN-106.M1 STEAM COOKER 2 EXHAUST FAN 3; 19: 19J RM6-SLT-201.M1 SLITTER
K
| L | 1: 01L 12" SPACE; 2: 02L RM6-MCC1-02L.SW1 ETHERNET SWITCH (20-PORT); 3: 03L 12" SPACE; 6: 06L RM6-MCC1-06L.SW1 ETHERNET SWITCH (20-PORT); 14: 14L RM6-MCC1-14L.SW1 ETHERNET SWITCH (20-PORT); 16: 16L 12" SPACE
M
RM6-6MCC02 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
| A | 01A MAIN INCOMING MCB | 02A RM6-MGR-101.M3 MIXER GRINDER 1 DISCHARGE SCREW | 03A RM6-BIN-101D.M1 SURGE BIN 4 AGITATOR | 04A RM6-BIN-101B.M1 SURGE BIN 2 AGITATOR | 05A RM6-PMP-103.M1 DUAL AUGER CART 1 PUMP | 06A RM6-SCR-201.M1 VIBRATORY SCREENER | 07A RM6-CNV-201.M1 INCLINE CONVEYOR | 08A RM6-PMP-101.M1 AUGER CART 1 PUMP | 09A 12" SPACE | 10A RM6-GRR-101.M1 FROZEN BLOCK BREAKER 1 | 11A RM6-GRR-101.M2 FROZEN BLOCK BREAKER 2 | 12A RM6-SKD-101.M2 VOTATOR PMP-202 COOKER 1 | 13A SPARE VFD - 1HP | 14A RM6-SKD-102.M1 VOTATOR PMP-101 COOKER 1 | 15A RM6-SKD-103.M2 VOTATOR PMP-202 COOKER 2 | 16A RM6-HTX-101.M1 VOTATOR HX-101 COOKER 1 | 17A RM6-HTX-103.M1 VOTATOR HX-103 COOKER 1 | 18A
B
| C | 9: 09C 12" SPACE; 18: 18C RM6-AGC-101.M1 AUGER CART 1 AUGER 1
D
| E | 6: 06E RM6-MGR-101.M1 RM6-MGR-101.M2 MIXER GRINDER 1; 7: 07E RM6-MGR-102.M1 RM6-MGR-102.M2 MIXER GRINDER 2; 9: 09E RM6-MLT-102.M1 COMBO TOTE DUMPER; 12: 12E RM6-SKD-102.M2 VOTATOR PMP-202 COOKER 2; 13: 13E RM6-CNV-108.M1 INCLINE CONVEYOR SCREW; 14: 14E RM6-CNV-102.M1 METAL DETECTOR BELT CONVEYOR; 15: 15E RM6-SKD-104.M1 VOTATOR PMP-101 COOKER 2
| F | 1: 01F RM6-MCC2-PM POWERMONITOR 5000 W/ ETHERNET
| G | 2: 02G RM6-SKD-101.M1 VOTATOR PMP-201 COOKER 1; 3: 03G RM6-BIN-101C.M1 SURGE BIN 3 AGITATOR; 4: 04G RM6-BIN-101A.M1 SURGE BIN 1 AGITATOR; 5: 05G RM6-PMP-104.M1 DUAL AUGER CART 2 PUMP; 9: 09G RM6-MGR-102.M3 MIXER GRINDER 2 DISCHARGE SCREW; 16: 16G RM6-HTX-102.M1 VOTATOR HX-102 COOKER 1; 17: 17G RM6-HTX-104.M1 VOTATOR HX-104 COOKER 1
| H | 8: 08H RM6-MTL-104.M1 MIXER GRINDER 2 COLUMN DUMPER; 18: 18H RM6-AGC-101.M2 AUGER CART 1 AUGER 2
| J | 1: 01J 6" SPACE; 12: 12J RM6-CNV-105.M1 SURGE BIN TAKEAWAY CONVEYOR; 14: 14J RM6-SKD-103.M1 VOTATOR PMP-201 COOKER 2; 15: 15J RM6-SKD-104.M2 VOTATOR PMP-102 COOKER 2
| K | 1: 01K RM6-MCC2-01K.PS1 ETHERNET SWITCH POWER SUPPLY
| L | 2: 02L RM6-MCC2-02L.SW1 ETHERNET SWITCH (20-PORT); 8: 08L RM6-MCC2-08L.SW1 ETHERNET SWITCH (20-PORT); 13: 13L RM6-MCC2-13L.SW1 ETHERNET SWITCH (20-PORT)
M
VTTRS-MCC1 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
| A | 01A MAIN INCOMING MCB | 02A 12" SPACE | 03A PMP-101 B&F HOT WATER LOOP PUMP | 04A PMP-102 BOOSTER PUMP | 05A RM5-MCC1-5A.SW1 ETHERNET SWITCH (20-PORT) | 06A PMP-106 CHILLED WATER PUMP 2 | 07A PMP-103 CHILLED WATER PUMP 1 | 08A 6" SPACE | 09A 6" SPACE | 10A 6" SPACE | 11A 12" SPACE | 12A 12" SPACE | 13A RM5-MCC1-13A.ENPS ETHERNET SWITCH POWER SUPPLY | 14A SPARE VFD - 2HP | 15A SPARE VFD - 2HP | 16A 6" SPACE | 17A RM5-MCC1-5A.SW1 ETHERNET SWITCH (20-PORT) | 18A 12" SPACE
| B | 8: 08B SPARE VFD - 10HP; 9: 09B FHD-101 FORMING HEAD; 10: 10B PMP-10x VOTATOR SKID HW CIRC PUMP; 16: 16B CNV-102 BATH CONVEYOR 2
| C | 2: 02C RL7-MCC1-PM POWERMONITOR 5000 W/ ETHERNET; 5: 05C 12" SPACE; 11: 11C PMP-104 INJECTION PUMP 1; 12: 12C SPARE VFD - 5HP; 13: 13C 12" SPACE; 17: 17C 6" SPACE; 18: 18C 12" SPACE
| D | 14: 14D SPARE VFD - 2HP; 15: 15D SPARE VFD - 2HP; 17: 17D SPARE VFD - 5HP
| E | 5: 05E 12" SPACE; 13: 13E 6" SPACE; 18: 18E 12" SPACE
| F |  | 02F HTX-101 VOTATOR 1 | 03F HTX-102 VOTATOR 2 | 04F HTX-103 VOTATOR 3 |  | 06F HTX-105 VOTATOR 5 | 07F HTX-104 VOTATOR 4 | 08F HTX-106 VOTATOR 6 | 09F HTX-107 VOTATOR 7 | 10F HTX-108 VOTATOR 8 | 11F HTX-109 VOTATOR 9 | 12F HTX-110 VOTATOR 10 | 13F CNV-101 BATH CONVEYOR 1 |  |  | 16F SPARE VFD - 30HP
| G | 5: 05G 12" SPACE; 14: 14G SPARE VFD - 5HP; 15: 15G PMP-109 BATH 1 CIRCULATION PUMP; 17: 17G SPARE VFD - 5HP; 18: 18G 12" SPACE
| H | 1: 01H 6" SPACE
| J | 1: 01J 12" SPACE; 5: 05J 12" SPACE; 18: 18J 12" SPACE
| K | 13: 13K PMP-106 VOTATOR SKID MAKEUP WATER PUMP; 14: 14K SPARE VFD - 5HP; 15: 15K SPARE VFD - 5HP; 17: 17K SCR-101 WASTE SEPARATOR DRUM
| L | 1: 01L 12" SPACE; 5: 05L RM5-MCC1-5L.ENPS ETHERNET SWITCH POWER SUPPLY; 18: 18L 12" SPACE
M
VTTRS-MCC2 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
| A | 01A MAIN INCOMING MCB | 02A 12" SPACE | 03A SPARE VFD - 15HP | 04A GRR-001 FROZEN GRINDER | 05A RM5-MCC2-5A.SW1 ETHERNET SWITCH (20-PORT) | 06A SPARE VFD - 5HP | 07A CNV-002 FB INCLINE / MD CONVEYOR | 08A MGR-001 DISCHARGE SCREW | 09A MLT-004 COLUMN DUMPER | 10A PMP-xxx INCLINE AUGER HYDRAULIC PUMP | 11A RM5-MCC2-11A.SW1 ETHERNET SWITCH (20-PORT) | 12A MLT-001 TOTE DUMPER | 13A 12" SPACE | 14A GRR-001 FROZEN GRINDER
B
| C | 2: 02C MGR-001 LEFT / RIGHT AUGER; 5: 05C 12" SPACE; 10: 10C MLT-005 COLUMN DUMPER; 11: 11C AGC-001.M1 AUGER CART 1 - LEFT AUGER; 12: 12C ??? TRACK; 13: 13C 12" SPACE
| D | 6: 06D AGC-002.M1 AUGER CART LEFT AUGER; 9: 09D CNV-002 INCLINE PIVOT AUGER
| E | 5: 05E 12" SPACE; 7: 07E 12" SPACE; 13: 13E 12" SPACE
| F | 3: 03F SPARE VFD - 30HP; 8: 08F GRR-002 FROZEN GRINDER SCREW; 10: 10F 6" SPACE; 11: 11F AGC-001.M2 AUGER CART 1 - RIGHT AUGER; 12: 12F AGC-001.M3 AUGER CART 1 - PUMP
| G | 5: 05G 12" SPACE; 6: 06G AGC-002.M2 AUGER CART RIGHT AUGER; 7: 07G 12" SPACE; 9: 09G TNK-001 COOKING KETTLE MIXER; 10: 10G 12" SPACE; 13: 13G 12" SPACE
| H | 1: 01H RL7-MCC1-PM POWERMONITOR 5000 W/ ETHERNET
| J | 5: 05J 12" SPACE; 7: 07J CNV-003 INCLINE AUGER CONVEYOR; 10: 10J 12" SPACE; 11: 11J AGC-002.M3 AUGER CART 2 - LEVELING RIBBON; 13: 13J 12" SPACE
| K | 6: 06K CNV-001 INCLINE BELT CONVEYOR; 9: 09K AGR-001 CHILLING KETTLE AGITATOR
| L | 1: 01L 12" SPACE; 5: 05L RM5-MCC1-5L.ENPS ETHERNET SWITCH POWER SUPPLY; 10: 10L 12" SPACE; 13: 13L 12" SPACE
M
UNUSED | bar: 1
| A | 1: 01A SPARE VFD - 75HP
B
C
D
E
F
G
H
J
K
L
M